## SCADA_Read
Cat® ECS 200 — Recommended SCADA Modbus Registers
DEVICE: ECS 200 Genset (200G) | [5 empty] | PORT 502 — READ Registers — Engine Sensor Data
Parameter Name | R/W | Holding Register | Hex Addr | Ct | Description | Scaling (Resolution) | Offset | Limits (Ranges) | Block ID | Addr-1 | Hex | 0x Addr
🛢️ BLOCK G1 — Read(41, 9) — Oil/Coolant/Fuel/Intake/Turbo
Oil Pressure | R | 41 | 0x0028 | 1 | Engine oil pressure | 1/128 psi / bit | 0 psi | 0 to 511 psi | G1
Coolant Temperature | R | 42 | 0x0029 | 1 | Engine coolant temperature | 1/32 °F / bit | -273 °F | -273 to 1775 °F | G1
Fuel Level | R | 43 | 0x002A | 1 | Fuel tank level | 1/2.56 % / bit | 0 % | 0 to 100 % | G1
Coolant Level | R | 44 | 0x002B | 1 | Coolant level sensor (if equipped) | 0.5 % / bit | 0 % | 0 to 100 % | G1
Oil Filter Differential Pressure | R | 45 | 0x002C | 1 | Oil filter dP (if equipped) | 1/128 psi / bit | 0 psi | 0 to 511 psi | G1
Intake Manifold Air Temperature | R | 46 | 0x002D | 1 | Intake manifold air temp | 1/32 °F / bit | -273 °F | -273 to 1775 °F | G1
Turbocharger Boost Pressure | R | 49 | 0x0030 | 1 | Turbocharger boost pressure | 1/128 psi / bit | 0 psi | 0 to 511 psi | G1
🌡️ BLOCK G2 — Read(57, 10) — Exhaust/Oil Temp/Fuel Rate/Hours
Exhaust Temperature Left Bank | R | 57 | 0x0038 | 1 | Exhaust manifold temperature — left bank | 1/32 °F / bit | -273 °F | -273 to 1775 °F | G2
Exhaust Temperature Right Bank | R | 58 | 0x0039 | 1 | Exhaust manifold temperature — right bank | 1/32 °F / bit | -273 °F | -273 to 1775 °F | G2
Oil Temperature | R | 59 | 0x003A | 1 | Engine oil temperature | 1/32 °F / bit | -273 °F | -273 to 1775 °F | G2
Fuel Consumption Rate | R | 62 | 0x003D | 1 | Instantaneous fuel consumption rate | 0.05 L/hr / bit | 0 L/hr | 0 to 3212.75 L/hr | G2
Engine Hours | R | 65 | 0x0040 | 2 | Total engine operating hours | 0.05 hr / bit | 0 hr | 0 to 210,554,060.75 hr | G2
↳ Engine Hours (LSW) |  | 66 | 0x0041 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | G2
🔧 BLOCK G3 — Read(154, 1) — Engine Speed
Engine Speed (RPM) | R | 154 | 0x0099 | 1 | Engine crankshaft speed | 0.125 rpm / bit | 0 rpm | 0 to 8031.875 rpm | G3

## Change History
Version | Change History | Notes
v1.0 | Initial recommended register list — curated from LEBE23522-00 SCADA Manual | ECS 200 v1.1 register list