## SCADA_Read
Cat® ECS 200 — Recommended SCADA Modbus Registers
DEVICE: ECS 200 Paralleling (200P) | [5 empty] | PORT 502 — READ Registers — 1-Second Fast Poll
Parameter Name | R/W | Holding Register | Hex Addr | Ct | Description | Scaling (Resolution) | Offset | Limits (Ranges) | Block ID | Addr-1 | Hex | 0x Addr
⚡ BLOCK P1 — Read(2, 4) — Event/Alarm Status
System Event Lamp Status | R | 2 | 0x0001 | 1 | Indicates system lamp status | Bits 15:4 Unused Bits 3:2 Amber Lamp (Boolean) Bits 1:0 Red Lamp (Boolean) |  | Bit-packed | P1
System Horn Active Status | R | 3 | 0x0002 | 1 | Indicates audible alert horn status | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  | 0–3 | P1
Hard Shutdown Status | R | 4 | 0x0003 | 1 | Indicates hard shutdown is active | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  | 0–3 | P1
Soft Shutdown Status | R | 5 | 0x0004 | 1 | Indicates soft shutdown is active | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  | 0–3 | P1
🔋 BLOCK P2 — Read(40, 1) — Battery
Battery Voltage | R | 40 | 0x0027 | 1 | DC battery voltage at controller input | 1/20 V / bit | 0 V | 0 to 3276.75 V | P2
🚨 BLOCK P3 — Read(101, 10) — User Alarm Groups
User Alarm Group A | R | 101 | 0x0064 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 1 = Alarm ON, 0 = Alarm OFF |  | Bit-packed | P3
User Alarm Group B | R | 102 | 0x0065 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group C | R | 103 | 0x0066 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group D | R | 104 | 0x0067 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group E | R | 105 | 0x0068 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group F | R | 106 | 0x0069 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group G | R | 107 | 0x006A | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group H | R | 108 | 0x006B | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group I | R | 109 | 0x006C | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group J | R | 110 | 0x006D | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
⚡ BLOCK P4 — Read(150, 10) — Generator Averages & Power
Generator Average Line-Line Voltage | R | 150 | 0x0095 | 1 | Average Line to Line RMS voltage at generator output | 1 V / bit | 0 V | 0 to 64255 V | P4
Generator Average Current | R | 152 | 0x0097 | 1 | Average RMS current at generator output | 1 A / bit | 0 A | 0 to 64255 A | P4
Engine Speed | R | 154 | 0x0099 | 1 | Engine RPM (from 200G via CAN) | 0.125 rpm / bit | 0 rpm | 0 to 8031.875 rpm | P4
Generator Total Real Power | R | 155 | 0x009A | 2 | Total real power (kW) delivered by the generator | 1 W / bit | -2000000000 W | -2B to +2.21B W | P4
↳ Generator Total Real Power (LSW) |  | 156 | 0x009B |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P4
Generator Frequency | R | 157 | 0x009C | 1 | Average AC frequency at generator output | 1/128 Hz / bit | 0 Hz | 0 to 501.99 Hz | P4
Generator Average Power Factor | R | 159 | 0x009E | 1 | Average power factor at generator output | 1/16384 / bit | -2 | -2.0 to +2.0 | P4
⚡ BLOCK P5 — Read(180, 12) — Per-Phase Voltage/Current/PF
Voltage L1-L2 | R | 180 | 0x00B3 | 1 | Line to Line RMS voltage phase A-B | 1 V / bit | 0 V | 0 to 64255 V | P5
Voltage L2-L3 | R | 181 | 0x00B4 | 1 | Line to Line RMS voltage phase B-C | 1 V / bit | 0 V | 0 to 64255 V | P5
Voltage L3-L1 | R | 182 | 0x00B5 | 1 | Line to Line RMS voltage phase C-A | 1 V / bit | 0 V | 0 to 64255 V | P5
Voltage L1-N | R | 183 | 0x00B6 | 1 | Line to Neutral RMS voltage phase A | 1 V / bit | 0 V | 0 to 64255 V | P5
Voltage L2-N | R | 184 | 0x00B7 | 1 | Line to Neutral RMS voltage phase B | 1 V / bit | 0 V | 0 to 64255 V | P5
Voltage L3-N | R | 185 | 0x00B8 | 1 | Line to Neutral RMS voltage phase C | 1 V / bit | 0 V | 0 to 64255 V | P5
Current L1 | R | 186 | 0x00B9 | 1 | RMS current phase A | 1 A / bit | 0 A | 0 to 64255 A | P5
Current L2 | R | 187 | 0x00BA | 1 | RMS current phase B | 1 A / bit | 0 A | 0 to 64255 A | P5
Current L3 | R | 188 | 0x00BB | 1 | RMS current phase C | 1 A / bit | 0 A | 0 to 64255 A | P5
Power Factor L1 | R | 189 | 0x00BC | 1 | Power factor phase A | 1/16384 / bit | -2 | -2.0 to +2.0 | P5
Power Factor L2 | R | 190 | 0x00BD | 1 | Power factor phase B | 1/16384 / bit | -2 | -2.0 to +2.0 | P5
Power Factor L3 | R | 191 | 0x00BE | 1 | Power factor phase C | 1/16384 / bit | -2 | -2.0 to +2.0 | P5
🔋 BLOCK P6 — Read(202, 5) — Reactive & Apparent Power
Generator Total Apparent Power | R | 202 | 0x00C9 | 2 | Total apparent power (kVA) delivered by the generator | 1 VA / bit | 0 VA | 0 to 4,294,967,295 VA | P6
↳ Generator Total Apparent Power (LSW) |  | 203 | 0x00CA |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P6
Generator Total Reactive Power | R | 205 | 0x00CC | 2 | Total reactive power (kVAR) delivered by the generator | 1 VAr / bit | -2000000000 VAr | -2B to +2.21B VAr | P6
↳ Generator Total Reactive Power (LSW) |  | 206 | 0x00CD |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P6
🔀 BLOCK P7 — Read(228, 5) — Operating State & Breaker
Genset Available Status | R | 228 | 0x00E3 | 1 | Whether the genset is available to the paralleling system | 0 = Not Available 1 = Available 2 = Error 3 = Disabled Or Not Available |  | 0–3 | P7
Generator Circuit Breaker Status | R | 229 | 0x00E4 | 1 | Status of the generator circuit breaker | 0 = Open 1 = Closed 2 = Error 3 = Disabled Or Not Available |  | 0–3 | P7
Operating Mode | R | 230 | 0x00E5 | 1 | Current operating mode of the genset controller | 0 = Off 1 = Manual 2 = Auto 3 = Test |  | 0–3 | P7
Genset Auto Start State | R | 231 | 0x00E6 | 1 | Current state of the automatic start/stop sequence | 0 = Init 1 = Pre Crank 2 = Starting 3 = Running 4 = Pre Cooldown 5 = Cooldown 6 = Stopping 7 = Stopped 8 = Idling |  | 0–8 | P7
Engine Run Status | R | 232 | 0x00E7 | 1 | Whether the engine is currently running | 0 = Off 1 = Running 2 = Error 3 = Disabled Or Not Available |  | 0–3 | P7
🔀 BLOCK P8 — Read(730, 9) — DBA & Sync Mode
Dead Bus Arbitration (DBA) State | R | 730 | 0x02D9 | 1 | Current state of dead bus arbitration logic | Enumerated — see SCADA manual §7.0 |  | Enumerated | P8
DBA Last Fail Reason | R | 731 | 0x02DA | 1 | Reason for last DBA failure | Enumerated failure codes |  | Enumerated | P8
Synchronize Mode / State | R | 738 | 0x02E1 | 1 | Current sync mode and state for paralleling | Enumerated — see SCADA manual §7.0 |  | Enumerated | P8
🔗 BLOCK P9 — Read(750, 31+) — System Totals & Per-Unit Data
Number of Units Online | R | 750 | 0x02ED | 1 | Total number of gensets currently online | 1 / bit | 0 | 0 to 32 | P9
Number of Units Available | R | 751 | 0x02EE | 1 | Total number of gensets available | 1 / bit | 0 | 0 to 32 | P9
Number of EPS Units Online | R | 752 | 0x02EF | 1 | Emergency Power Supply units online | 1 / bit | 0 | 0 to 32 | P9
Number of EPS Units Available | R | 753 | 0x02F0 | 1 | Emergency Power Supply units available | 1 / bit | 0 | 0 to 32 | P9
System Total Real Power | R | 756 | 0x02F3 | 2 | Combined real power from all online gensets | 1 W / bit | -2000000000 W | -2B to +2.21B W | P9
↳ System Total Real Power (LSW) |  | 757 | 0x02F4 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P9
System Total Percent Load | R | 758 | 0x02F5 | 1 | System-wide percent of rated load | 0.4 % / bit | 0 % | 0 to 100 % | P9
Gen #1 — Warning Status | R | 759 | 0x02F6 | 1 | Gen #1 has active warning | 0 = False, 1 = True |  | 0–1 | P9
Gen #1 — Shutdown Status | R | 760 | 0x02F7 | 1 | Gen #1 has active shutdown | 0 = False, 1 = True |  | 0–1 | P9
Gen #1 — DBA Status | R | 761 | 0x02F8 | 1 | Gen #1 dead bus arbitration status | Enumerated DBA states |  | Enumerated | P9
Gen #1 — Load Share Status | R | 762 | 0x02F9 | 1 | Gen #1 load share state | Enumerated load share states |  | Enumerated | P9
Gen #1 — Average Voltage | R | 763 | 0x02FA | 1 | Gen #1 average line-line voltage | 1 V / bit | 0 V | 0 to 64255 V | P9
Gen #1 — Frequency | R | 764 | 0x02FB | 1 | Gen #1 AC frequency | 1/128 Hz / bit | 0 Hz | 0 to 501.99 Hz | P9
Gen #1 — Real Power | R | 765 | 0x02FC | 2 | Gen #1 real power output | 1 W / bit | -2000000000 W | -2B to +2.21B W | P9
↳ Gen #1 — Real Power (LSW) |  | 766 | 0x02FD |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P9
Gen #1 — Breaker Status | R | 767 | 0x02FE | 1 | Gen #1 circuit breaker position | 0 = Open 1 = Closed 2 = Error 3 = N/A |  | 0–3 | P9
Gen #1 — Operating Mode | R | 768 | 0x02FF | 1 | Gen #1 operating mode | 0 = Off 1 = Manual 2 = Auto 3 = Test |  | 0–3 | P9
Gen #1 — Genset Available | R | 769 | 0x0300 | 1 | Gen #1 availability | 0 = Not Available 1 = Available |  | 0–1 | P9
Gen #1 — Engine Run Status | R | 770 | 0x0301 | 1 | Gen #1 engine running | 0 = Off 1 = Running |  | 0–1 | P9
Gen #1 — % Rated kW Load | R | 780 | 0x030B | 1 | Gen #1 percent of rated kW | 0.4 % / bit | 0 % | 0 to 100 % | P9

## Change History
Version | Change History | Notes
v1.0 | Initial recommended register list — curated from LEBE23522-00 SCADA Manual | ECS 200 v1.1 register list