## SCADA_Read
Cat® ECS 200 — Recommended SCADA Modbus Registers
DEVICE: ECS 200 Paralleling (200P) | [5 empty] | PORT 502 — READ Registers — 5–30 Second Slow Poll
Parameter Name | R/W | Holding Register | Hex Addr | Ct | Description | Scaling (Resolution) | Offset | Limits (Ranges) | Block ID | Addr-1 | Hex | 0x Addr
📈 BLOCK P10 — Read(208, 13) — Energy Meters & Ratings
Positive Real Energy (kWh) | R | 208 | 0x00CF | 2 | Accumulated positive real energy | 1 Wh / bit | 0 Wh | 0 to 4.29B Wh | P10
↳ Positive Real Energy (kWh) (LSW) |  | 209 | 0x00D0 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P10
Positive Reactive Energy (kVARh) | R | 210 | 0x00D1 | 2 | Accumulated positive reactive energy | 1 VARh / bit | 0 VARh | 0 to 4.29B VARh | P10
↳ Positive Reactive Energy (kVARh) (LSW) |  | 211 | 0x00D2 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P10
Negative Real Energy (kWh) | R | 212 | 0x00D3 | 2 | Accumulated negative real energy (reverse power) | 1 Wh / bit | 0 Wh | 0 to 4.29B Wh | P10
↳ Negative Real Energy (kWh) (LSW) |  | 213 | 0x00D4 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P10
Rated Line-Line Voltage | R | 214 | 0x00D5 | 1 | Generator nameplate rated voltage | 1 V / bit | 0 V | 0 to 64255 V | P10
Rated Line-Neutral Voltage | R | 215 | 0x00D6 | 1 | Generator nameplate rated L-N voltage | 1 V / bit | 0 V | 0 to 64255 V | P10
Rated Current | R | 216 | 0x00D7 | 1 | Generator nameplate rated current | 1 A / bit | 0 A | 0 to 64255 A | P10
Rated Frequency | R | 217 | 0x00D8 | 1 | Generator nameplate rated frequency | 1/128 Hz / bit | 0 Hz | 0 to 501.99 Hz | P10
Rated Real Power | R | 218 | 0x00D9 | 2 | Generator nameplate rated power | 1 W / bit | -2000000000 W | -2B to +2.21B W | P10
↳ Rated Real Power (LSW) |  | 219 | 0x00DA |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P10
Rated Power Factor | R | 220 | 0x00DB | 1 | Generator nameplate rated power factor | 1/16384 / bit | -2 | -2.0 to +2.0 | P10
🕐 BLOCK P11 — Read(245, 3) — Real-Time Clock
Date (MM/DD packed) | R | 245 | 0x00F4 | 1 | Controller real-time clock date | See SCADA manual §7.12 for byte decode |  | Packed bytes | P11
Year | R | 246 | 0x00F5 | 1 | Controller real-time clock year | See SCADA manual §7.12 for byte decode |  | Packed bytes | P11
Time (HH:MM:SS packed) | R | 247 | 0x00F6 | 1 | Controller real-time clock time | See SCADA manual §7.12 for byte decode |  | Packed bytes | P11
🌐 BLOCK P12 — Read(350, 1) — Data Link Status
Primary Data Link Status | R | 350 | 0x015D | 1 | CAN datalink health indicator | 00 = OK 01 = Fault 11 = Disabled Or Not Available |  | 0, 1, 3 | P12
🌐 BLOCK P13 — Read(577, 6) — Ethernet Port Status
Ethernet 2-Wire Port A Status | R | 577 | 0x0240 | 1 | SPE port A enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
Ethernet 2-Wire Port B Status | R | 578 | 0x0241 | 1 | SPE port B enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
Ethernet 4-Wire Port #1 Status | R | 579 | 0x0242 | 1 | Ethernet port #1 enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
Ethernet 4-Wire Port #2 Status | R | 580 | 0x0243 | 1 | Ethernet port #2 enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
Ethernet 4-Wire Port #3 Status | R | 581 | 0x0244 | 1 | Ethernet port #3 enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
Ethernet 4-Wire Port #4 Status | R | 582 | 0x0245 | 1 | Ethernet port #4 enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
🔌 BLOCK P14 — Read(700, 16) — Onboard I/O Status
Onboard Discrete Input Status | R | 700 | 0x02BB | 1 | DI 1–12 status bit-packed | Bit 0–11 = DI1–DI12 1 = Active, 0 = Inactive |  | Bit-packed | P14
Onboard Isolated DI Status | R | 701 | 0x02BC | 1 | Isolated digital input status | Bit 0 = Isolated DI |  | Bit-packed | P14
Onboard Discrete Output Status | R | 702 | 0x02BD | 1 | DO 1–12 status bit-packed | Bit 0–11 = DO1–DO12 1 = Active, 0 = Inactive |  | Bit-packed | P14
Onboard Analog Input #1 Value | R | 703 | 0x02BE | 1 | AI #1 sensor value — scaling depends on Cat ET configuration | Sensor-dependent | Sensor-dependent | Sensor-dependent | P14
Onboard Analog Input #2 Value | R | 704 | 0x02BF | 1 | AI #2 sensor value | Sensor-dependent | Sensor-dependent | Sensor-dependent | P14
Onboard Analog Input #3 Value | R | 705 | 0x02C0 | 1 | AI #3 sensor value | Sensor-dependent | Sensor-dependent | Sensor-dependent | P14
Onboard Analog Output #1 Value | R | 706 | 0x02C1 | 2 | AO #1 output value | Configured output | See Cat ET | Configured | P14
↳ Onboard Analog Output #1 Value (LSW) |  | 707 | 0x02C2 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P14
Onboard Analog Output #2 Value | R | 708 | 0x02C3 | 2 | AO #2 output value | Configured output | See Cat ET | Configured | P14
↳ Onboard Analog Output #2 Value (LSW) |  | 709 | 0x02C4 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P14
Onboard PWM Output #1 Value | R | 710 | 0x02C5 | 2 | PWM #1 output value | Configured output | See Cat ET | Configured | P14
↳ Onboard PWM Output #1 Value (LSW) |  | 711 | 0x02C6 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P14
Onboard PWM Output #2 Value | R | 712 | 0x02C7 | 2 | PWM #2 output value | Configured output | See Cat ET | Configured | P14
↳ Onboard PWM Output #2 Value (LSW) |  | 713 | 0x02C8 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P14
Onboard PWM Output #3 Value | R | 714 | 0x02C9 | 2 | PWM #3 output value | Configured output | See Cat ET | Configured | P14
↳ Onboard PWM Output #3 Value (LSW) |  | 715 | 0x02CA |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P14
⚖️ BLOCK P15 — Read(1465, 5) — LSLD State & Timers
LSLD Priority Mode | R | 1465 | 0x05B8 | 1 | Load Sense Load Demand sequencing priority | First On-First Off, Hourmeter, Manual, FIFO-EPS… |  | Enumerated | P15
LSLD State | R | 1466 | 0x05B9 | 1 | Current LSLD state | Idle, Adding, Removing, Load Shed… |  | Enumerated | P15
LSLD Desired Units Online | R | 1467 | 0x05BA | 1 | Number of units LSLD wants online | 1 / bit | 0 | 0 to 32 | P15
LSLD Add Timer Remaining | R | 1468 | 0x05BB | 1 | Seconds remaining before next unit add | 1 s / bit | 0 s | 0 to 65535 s | P15
LSLD Remove Timer Remaining | R | 1469 | 0x05BC | 1 | Seconds remaining before next unit remove | 1 s / bit | 0 s | 0 to 65535 s | P15
⚖️ BLOCK P16 — Read(1737, 1) — Load Setpoint
Generator Real Load Control Base Load Setpoint | R | 1737 | 0x06C8 | 1 | Active base load setpoint as % of rated power | 0.01 % / bit | -321.27 % | -321.27 to 321.28 % | P16
⚖️ BLOCK P17 — Read(1805, 1) — Load Control State
Generator Real Load Control State | R | 1805 | 0x070C | 1 | Current load control mode | Isochronous, Base Load, Droop, Import/Export… |  | Enumerated | P17

## Change History
Version | Change History | Notes
v1.0 | Initial recommended register list — curated from LEBE23522-00 SCADA Manual | ECS 200 v1.1 register list