## SCADA_Write
Cat® ECS 200 — Recommended SCADA Modbus Registers
DEVICE: ECS 200 Paralleling (200P) | [5 empty] | PORT 50200 — WRITE Registers — Commands & Setpoints (FC16)
Parameter Name | R/W | Holding Register | Hex Addr | Ct | Description | Scaling (Resolution) | Offset | Limits (Ranges) | Block ID | Addr-1 | Hex | 0x Addr
🚦 Alarm Acknowledge & Reset
Alarm Acknowledge Command | R | 1 | 0x0000 | 1 | Acknowledge active alarms | 0 = FALSE 1 = TRUE |  | 0–1 | W-CMD
Reset All Events Command | R | 2 | 0x0001 | 1 | Reset all active events | 0 = FALSE 1 = TRUE |  | 0–1 | W-CMD
🔀 Mode & Start/Stop Commands
Auto Mode Command | R | 102 | 0x0065 | 1 | Command genset operating mode | Enumerated mode commands |  | Enumerated | W-CMD
Start Command | R | 103 | 0x0066 | 1 | Engine start command | 0 = Off 1 = Start 2 = Error 3 = N/A |  | 0–3 | W-CMD
Stop Command | R | 104 | 0x0067 | 1 | Engine stop command | 0 = Off 1 = Stop 2 = Error 3 = N/A |  | 0–3 | W-CMD
⚖️ Setpoint Commands
Base Load Setpoint (kW) | R | 6 | 0x0005 | 2 | Target base load real power setpoint | 1 W / bit | -2000000000 W | -2B to +2.21B W | W-SET
↳ Base Load Setpoint (kW) (LSW) |  | 7 | 0x0006 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | W-SET
Base PF Setpoint | R | 8 | 0x0007 | 2 | Target base power factor setpoint | 1/16384 / bit | -2 | -2.0 to +2.0 | W-SET
↳ Base PF Setpoint (LSW) |  | 9 | 0x0008 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | W-SET
Base VAR Setpoint | R | 10 | 0x0009 | 2 | Target base reactive power setpoint | 1 VAr / bit | -2000000000 VAr | -2B to +2.21B VAr | W-SET
↳ Base VAR Setpoint (LSW) |  | 11 | 0x000A |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | W-SET
Base Frequency Setpoint | R | 12 | 0x000B | 2 | Target frequency bias setpoint | 1/128 Hz / bit | 0 Hz | 0 to 501.99 Hz | W-SET
↳ Base Frequency Setpoint (LSW) |  | 13 | 0x000C |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | W-SET
Base Voltage Setpoint | R | 14 | 0x000D | 2 | Target voltage bias setpoint | 1/128 V / bit | 0 V | 0 to 511.99 V | W-SET
↳ Base Voltage Setpoint (LSW) |  | 15 | 0x000E |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | W-SET

## Change History
Version | Change History | Notes
v1.0 | Initial recommended register list — curated from LEBE23522-00 SCADA Manual | ECS 200 v1.1 register list