## SCADA_Read
Cat® ECS 200 — Recommended SCADA Modbus Registers
DEVICE: ECS 200 Paralleling (200P) | [5 empty] | PORT 50201 — READ Registers — Module Status & Annunciator
Parameter Name | R/W | Holding Register | Hex Addr | Ct | Description | Scaling (Resolution) | Offset | Limits (Ranges) | Block ID | Addr-1 | Hex | 0x Addr
🌐 BLOCK S1 — Read(1, 2) — Module Online Status
Paralleling Controller Online | R | 1 | 0x0000 | 1 | Whether the paralleling controller is on the network (always True for self) | 0 = Offline 1 = Online |  | 0–1 | S1
Engine ECM Online | R | 2 | 0x0001 | 1 | Whether the engine ECM is communicating via CAN | 0 = Offline 1 = Online |  | 0–1 | S1
📊 BLOCK S2 — Read(16, 1) — Active Event Counts
Number of Active Events — Genset Controller | R | 16 | 0x000F | 1 | Count of currently active events on genset controller | 1 / bit | 0 | 0 to 65535 | S2
🔔 BLOCK S3 — Read(611, 23) — Annunciator Status Points
E-Stop Active | R | 611 | 0x0262 | 1 | Engine Auxiliary Switch Status (Emergency Stop) — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Generator Not In Auto Warning | R | 612 | 0x0263 | 1 | Generator control not in automatic mode — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Overcrank (Failure to Start) | R | 613 | 0x0264 | 1 | Engine failed to start within crank time — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Overspeed | R | 614 | 0x0265 | 1 | Engine overspeed detected — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
EPS Supplying Load | R | 615 | 0x0266 | 1 | Emergency Power Supply is active — GREEN | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Overload / Load Shed Contact | R | 616 | 0x0267 | 1 | Overload alarm or load shed active — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
High Coolant Temperature (Warning) | R | 617 | 0x0268 | 1 | Coolant temp warning threshold — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
High Coolant Temperature (Shutdown) | R | 618 | 0x0269 | 1 | Coolant temp shutdown threshold — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Coolant Temperature Warning | R | 619 | 0x026A | 1 | Coolant temp low warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Cranking Voltage Warning | R | 620 | 0x026B | 1 | Battery voltage too low for cranking — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Air Damper Shutdown | R | 621 | 0x026C | 1 | Air damper failure shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
High Battery Voltage (Warning) | R | 622 | 0x026D | 1 | Battery voltage high warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
High Battery Voltage (Shutdown) | R | 623 | 0x026E | 1 | Battery voltage high shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Battery Voltage Warning | R | 624 | 0x026F | 1 | Battery voltage low warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Oil Pressure (Warning) | R | 625 | 0x0270 | 1 | Oil pressure low warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Oil Pressure (Shutdown) | R | 626 | 0x0271 | 1 | Oil pressure low shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Coolant Level (Warning) | R | 627 | 0x0272 | 1 | Coolant level low warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Coolant Level (Shutdown) | R | 628 | 0x0273 | 1 | Coolant level low shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Fuel Level (Warning) | R | 629 | 0x0274 | 1 | Fuel level low warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Fuel Level (Shutdown) | R | 630 | 0x0275 | 1 | Fuel level low shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Battery Charger AC Failure | R | 631 | 0x0276 | 1 | Battery charger AC supply failure — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
SCR SPN 4792 (Warning) | R | 632 | 0x0277 | 1 | SCR aftertreatment warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
SCR SPN 4792 (Shutdown) | R | 633 | 0x0278 | 1 | SCR aftertreatment shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3

## Change History
Version | Change History | Notes
v1.0 | Initial recommended register list — curated from LEBE23522-00 SCADA Manual | ECS 200 v1.1 register list