## SCADA_Read
Cat® ECS 200 Genset SCADA Modbus Read Registers
SCADA IP ADDRESS (CONFIGURABLE) | [5 empty] | PORT NUMBER 502
Parameter Name | R/W | Holding Register |  | Ct | Description | Scaling(Resolution) | Offset | Limits(Ranges)
Engine Operating Mode | R | 1 | 0x000 | 1 | Indicates the status of the Generator system | 0 = STOP 1 = AUTO 2 = RUN |  |  | Engine Operating Mode | 0 | 0 | 0x000
System Event Lamp Status | R | 2 | 0x001 | 1 | Indicates the system status of the lamp | Bits 15:4 UNUSED Bits 3:2 Amber Lamp Status (Boolean) Bits 1:0 Red Lamp Status (Boolean) |  |  | Event Lamp Status | 1 | 1 | 0x001
System Horn Active Status | R | 3 | 0x002 | 1 | Indicates the status of the system horn (audible alert). | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 2 | 2 | 0x002
Hard Shutdown Status | R | 4 | 0x003 | 1 | Indicates status of hard shutdown | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 3 | 3 | 0x003
Soft Shutdown Status | R | 5 | 0x004 | 1 | indicates status of soft shutdown | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 4 | 4 | 0x004
Automatic Start/Stop State | R | 6 | 0x005 | 1 | Current state of the Automatic Start/Stop sequence. Either read from engine (if Engine ECM controls start/stop) or determined by Genset controller | 0 = INIT 1 = PRE CRANK 2 = STARTING 3 = RUNNING 4 = PRE COOLDOWN 5 = COOLDOWN 6 = STOPPING 7 = STOPPED 8 = IDLING |  |  | Engine Control State | 5 | 5 | 0x005
Generator Average Line-Line AC RMS Voltage | R | 7 | 0x006 | 1 | Average Line to Line RMS voltage measured at the generator output | 1 V / bit | 0 V | 0 to 64255 V | AC RMS Voltage | 6 | 6 | 0x006
Generator Average AC RMS Current | R | 8 | 0x007 | 1 | Average RMS current measured at the generator output. | 1 A / bit | 0 A | 0 to 64255 A | AC RMS Current | 7 | 7 | 0x007
Generator Average AC RMS Frequency | R | 9 | 0x008 | 1 | Average AC frequency measured at the generator output. | 1/128 Hz / bit | 0 Hz | 0 to 501.9922 Hz | AC Frequency | 8 | 8 | 0x008
Generator Overall Power Factor | R | 10 | 0x009 | 1 | The average Power Factor of the generator. | 1/16384 / bit | -1 | -1.0 to 1.0 | AC Power Factor | 9 | 9 | 0x009
Generator Overall Power Factor Lagging | R | 11 | 0x00A | 1 | Lead/lag status for generator average Power Factor. | 0 = Power factor leading 1 = Power factor lagging |  |  | AC Power Factor Lagging | 10 | A | 0x00A
Generator Total Real Power | R | 12 | 0x00B | 2 | Total real power delivered by the generator. | 1 W / bit | -2000000000 W | -2000000000 to +2211081215 W | AC Real Power | 11 | B | 0x00B
Generator Total Reactive Power | R | 14 | 0x00D | 2 | Total reactive power delivered by the generator. | 1 VAr / bit | -2000000000 VAr | -2000000000 to +2211081215 VAr | AC Reactive Power | 13 | D | 0x00D
Generator Total Apparent Power | R | 16 | 0x00F | 2 | The total apparent power delivered by the generator. | 1 VA / bit | -2000000000 VA | -2000000000 to +2211081215 VA | AC Apparent Power | 15 | F | 0x00F
Bus Average Line-Line AC RMS Voltage | R | 18 | 0x0011 | 1 | Line to Line RMS voltage measured at the generator phase AB output | 1 V / bit | 0 V | 0 to 64255 V | AC RMS Voltage | 17 | 11 | 0x0011
Bus Average AC RMS Frequency | R | 19 | 0x0012 | 1 | Indicates BUS average AC RMS frequency | 1/128 Hz / bit | 1 Hz | 1 to 501.9922 Hz | AC Frequency | 18 | 12 | 0x0012
Generator/Bus Phase Difference | R | 20 | 0x0013 | 1 | Line to Line RMS voltage measured at the generator phase CA output | 1 V / bit | 0 V | 0 to 64255 V | J1939 Angle 1 | 19 | 13 | 0x0013
Generator Phase A Line-Line AC RMS Voltage | R | 21 | 0x0014 | 1 | Line to Neutral RMS voltage measured at the generator phase A output. | 1 V / bit | 0 V | 0 to 64255 V | AC RMS Voltage | 20 | 14 | 0x0014
Generator Phase B Line-Line AC RMS Voltage | R | 22 | 0x0015 | 1 | Line to Neutral RMS voltage measured at the generator phase B output. | 1 V / bit | 0 V | 0 to 64255 V | AC RMS Voltage | 21 | 15 | 0x0015
Generator Phase C Line-Line AC RMS Voltage | R | 23 | 0x0016 | 1 | Line to Neutral RMS voltage measured at the generator phase C output. | 1 V / bit | 0 V | 0 to 64255 V | AC RMS Voltage | 22 | 16 | 0x0016
Generator Phase A AC RMS Current | R | 24 | 0x0017 | 1 | RMS current measured at the generator phase A output. | 1 A / bit | 0 A | 0 to 64255 A | AC RMS Current | 23 | 17 | 0x0017
Generator Phase B AC RMS Current | R | 25 | 0x0018 | 1 | RMS current measured at the generator phase B output. | 1 A / bit | 0 A | 0 to 64255 A | AC RMS Current | 24 | 18 | 0x0018
Generator Phase C AC RMS Current | R | 26 | 0x0019 | 1 | RMS current measured at the generator phase C output. | 1 A / bit | 0 A | 0 to 64255 A | AC RMS Current | 25 | 19 | 0x0019
Generator Phase A Line-Neutral AC RMS Voltage | R | 27 | 0x001A | 1 | Line to Neutral RMS voltage measured at the generator phase A output. | 1 V / bit | 0 V | 0 to 64255 V | AC RMS Voltage | 26 | 1A | 0x001A
Generator Phase B Line-Neutral AC RMS Voltage | R | 28 | 0x001B | 1 | Line to Neutral RMS voltage measured at the generator phase B output. | 1 V / bit | 0 V | 0 to 64255 V | AC RMS Voltage | 27 | 1B | 0x001B
Generator Phase C Line-Neutral AC RMS Voltage | R | 29 | 0x001C | 1 | Line to Neutral RMS voltage measured at the generator phase C output. | 1 V / bit | 0 V | 0 to 64255 V | AC RMS Voltage | 28 | 1C | 0x001C
Generator Total kW Hours | R | 30 | 0x001D | 2 | The total kilowatt-hours that have been exported by the generator. | 1 kWh / bit | 0 kWh | 0 to 4211081215 kWh | AC Kilowatt-hour | 29 | 1D | 0x001D
Generator Total kVAr Hours | R | 32 | 0x001F | 2 | The total kilovar-hours that have been imported by the generator. | 1 kVArh/bit | 0 kVArh | 0 to 4211081215 kVArh | AC Kilovar-hour | 31 | 1F | 0x001F
Generator Total kVAr Hours (leading) | R | 34 | 0x0021 | 2 | The total kilovar-hours that have been exported by the generator. | 1 kVArh/bit | 0 kVArh | 0 to 4211081215 kVArh | AC Kilovar-hour | 33 | 21 | 0x0021
Generator Total Percent kW | R | 36 | 0x0023 | 1 | Total real power delivered by the generator, as a percentage of generated rated power | 0.0078125 % / bit | -251 % | -251 to 250.99 % | Percent | 35 | 23 | 0x0023
Generator Total Percent kVAr | R | 37 | 0x0024 | 1 | The total reactive power delivered by the generator, as a percentage of generator rated reactive power. | 0.0078125 % / bit | -251 % | -251 to 250.99 % | Percent | 36 | 24 | 0x0024
Generator Average Line-Line AC RMS Voltage Percent | R | 38 | 0x0025 | 1 | The total kilovar-hours that have been exported by the generator. | 0.0078125 % / bit | -251 % | -251 to 250.99 % | Percent | 37 | 25 | 0x0025
Generator Average AC RMS Frequency Percent | R | 39 | 0x0026 | 1 | Average AC frequency percent measured at the generator output. | 0.0078125 % / bit | -251 % | -251 to 250.99 % | Percent | 38 | 26 | 0x0026
Battery Voltage | R | 40 | 0x0027 | 1 | Shows the Battery Voltage, as read at the input to the Genset Control | 0.05 V / bit | 0 V | 0 to 3212.75 V | J1939 Electrical Potential | 39 | 27 | 0x0027
Engine Oil Pressure | R | 41 | 0x0028 | 1 | Gauge pressure of oil in engine lubrication system as provided by oil pump. | 0.125 kPa / bit | 0 kPa | 0 to 8031.875 kPa | J1939 Pressure 5 | 40 | 28 | 0x0028
Engine Coolant Temperature | R | 42 | 0x0029 | 1 | Temperature of liquid found in engine cooling system. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 41 | 29 | 0x0029
Engine Operating Hours | R | 43 | 0x002A | 2 | Accumulated time that the engine is running. | 0.05 hour / bit | 0 hr | 0 to 210554060.75 hour | J1939 Time 10 | 42 | 2A | 0x002A
Air Filter 1 Differential Pressure from Data Link | R | 45 | 0x002C | 1 | Change in engine air system pressure, measured across the filter, due to the filter and any accumulation of solid foreign matter on or in the filter, as received from another module on the CAN Data Link. | 1 / 128 kPa / bit | -250 kPa | -250 to 251.99 kPa | J1939 Pressure 3 | 44 | 2C | 0x002C
Intake Manifold #1 Temperature from Data Link | R | 46 | 0x002D | 1 | Temperature of pre-combustion air found in intake manifold #1 of engine air supply system, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 45 | 2D | 0x002D
Total Fuel Consumption from Data Link | R | 47 | 0x002E | 2 | Total amount of fuel used by engine, as received from another module on the CAN Data Link. | 0.5 L / bit | 0 L | 0 to 2105540607.5 L | J1939 Volume | 46 | 2E | 0x002E
Turbocharger 1 Compressor Inlet Temperature | R | 49 | 0x0030 | 1 | Temperature of the air entering the compressor side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 48 | 30 | 0x0030
Turbocharger 2 Compressor Inlet Temperature | R | 50 | 0x0031 | 1 | Temperature of the air entering the compressor side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 49 | 31 | 0x0031
Turbocharger 3 Compressor Inlet Temperature | R | 51 | 0x0032 | 1 | Temperature of the air entering the compressor side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 50 | 32 | 0x0032
Turbocharger 4 Compressor Inlet Temperature | R | 52 | 0x0033 | 1 | Temperature of the air entering the compressor side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 51 | 33 | 0x0033
Oil Filter Differential Pressure from Data Link | R | 53 | 0x0034 | 1 | Change in engine oil pressure, measured across the filter, due to the filter and any accumulation of solid or semisolid material on or in the filter, as received from another module on the CAN Data Link. | 0.125 kPa / bit | 0 kPa | 0 to 8031.875 kPa | J1939 Pressure 5 | 52 | 34 | 0x0034
Fuel Filter Differential Pressure from Data Link | R | 54 | 0x0035 | 1 | Change in fuel delivery pressure, measured across the filter, due to accumulation of solid or semisolid matter on the filter element, as received from another module on the CAN Data Link. | 0.125 kPa / bit | 0 kPa | 0 to 8031.875 kPa | J1939 Pressure 5 | 53 | 35 | 0x0035
Fuel Level from Data Link | R | 55 | 0x0036 | 1 | Fuel level, as received from another module on the CAN Data Link. For legacy support only. For new applications, use register 198. | 0.0078125 % / bit | -251 % | -251 to 250.99 % | Percent | 54 | 36 | 0x0036
Engine rpm | R | 56 | 0x0037 | 1 | Engine rotational speed calculated in revolutions per minute. | 0.125 rpm / bit | 0 rpm | 0 to 8031.875 rpm | J1939 Rot Vel 1 | 55 | 37 | 0x0037
Exhaust Manifold #1 Temperature from Data Link | R | 57 | 0x0038 | 1 | Temperature of combustion byproducts within the left engine exhaust manifold, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 56 | 38 | 0x0038
Exhaust Manifold #2 Temperature from Data Link | R | 58 | 0x0039 | 1 | Temperature of combustion byproducts within the left engine exhaust manifold, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 57 | 39 | 0x0039
Engine Oil Temperature | R | 59 | 0x003A | 1 | Oil temp, independent of source. I/o pin (if configured) takes precedence over datalink. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 58 | 3A | 0x003A
Engine Fuel Temperature from Data Link | R | 60 | 0x003B | 1 | Temperature of the engine fuel as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 59 | 3B | 0x003B
Fuel Pressure | R | 61 | 0x003C | 1 | Gauge pressure of fuel in system as delivered from supply pump to the injection pump, as received from another module on the CAN Data Link. | 0.125 kPa / bit | 0 kPa | 0 to 8031.875 kPa | J1939 Pressure 5 | 60 | 3C | 0x003C
Crankcase Pressure from Data Link | R | 62 | 0x003D | 1 | Gauge pressure inside engine crankcase, as received from another module on the CAN Data Link. | 1 / 128 kPa / bit | -250 kPa | -250 to 251.99 kPa | J1939 Pressure 3 | 61 | 3D | 0x003D
Boost Pressure from Data Link | R | 63 | 0x003E | 1 | Gauge pressure of air measured downstream on the compressor discharge side of the turbocharger, as received from another module on the CAN Data Link. | 0.125 kPa / bit | 0 kPa | 0 to 8031.875 kPa | J1939 Pressure 5 | 62 | 3E | 0x003E
Engine Air Filter #2 Differential Pressure | R | 64 | 0x003F | 1 | Engine Air Filter #2 Differential Pressure | 0.05 kPa / bit | 0 kPa | 0 to 12.5 kPa | J1939 Pressure 8 | 63 | 3F | 0x003F
Instantaneous Fuel Consumption from Data Link | R | 65 | 0x0040 | 1 | Amount of fuel used by engine per unit time, as received from another module on the CAN Data Link. | 0.05 L/h per bit | 0 L/h | 0 to 3212.75 L/h | J1939 Flow Rate Liquid | 64 | 40 | 0x0040
Atmospheric Pressure from Data Link | R | 66 | 0x0041 | 1 | Absolute air pressure of the atmosphere, as received from another module on the CAN Data Link. | 0.125 kPa / bit | 0 kPa | 0 to 8031.875 kPa | J1939 Pressure 5 | 65 | 41 | 0x0041
Turbocharger 1 Turbine Inlet Temperature | R | 67 | 0x0042 | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 66 | 42 | 0x0042
Turbocharger 1 Turbine Outlet Temperature | R | 68 | 0x0043 | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 67 | 43 | 0x0043
Turbocharger 2 Turbine Inlet Temperature | R | 69 | 0x0044 | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 68 | 44 | 0x0044
Turbocharger 2 Turbine Outlet Temperature | R | 70 | 0x0045 | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 69 | 45 | 0x0045
Turbocharger 3 Turbine Inlet Temperature | R | 71 | 0x0046 | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 70 | 46 | 0x0046
Turbocharger 3 Turbine Outlet Temperature | R | 72 | 0x0047 | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 71 | 47 | 0x0047
Turbocharger 4 Turbine Inlet Temperature | R | 73 | 0x0048 | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 72 | 48 | 0x0048
Turbocharger 4 Turbine Outlet Temperature | R | 74 | 0x0049 | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 73 | 49 | 0x0049
Compressor Inlet Air Temperature from Data Link | R | 75 | 0x004A | 1 | Temperature of air entering vehicle air induction system | 1 C / bit | -40 C | -40 to 210 C | J1939 Temperature 1 | 74 | 4A | 0x004A
Left Turbo Inlet Pressure from Data Link | R | 76 | 0x004B | 1 | Gage pressure of the air entering the compressor side of the turbocharger from Data Link | 1 / 128 kPa / bit | -250 kPa | -250 to 251.99 kPa | J1939 Pressure 3 | 75 | 4B | 0x004B
Right Turbo Inlet Pressure from Data Link | R | 77 | 0x004C | 1 | Gage pressure of the air entering the compressor side of the turbocharger from Data Link | 1 / 128 kPa / bit | -250 kPa | -250 to 251.99 kPa | J1939 Pressure 3 | 76 | 4C | 0x004C
Engine Aftercooler Inlet Temperature from Data Link | R | 78 | 0x004D | 1 | Engine Aftercooler Inlet Temperature from Data Link | 1 C / bit | -40 C | -40 to 210 C | J1939 Temperature 1 | 77 | 4D | 0x004D
Engine Aftercooler Outlet Temperature from Data Link | R | 79 | 0x004E | 1 | Engine Aftercooler Outlet Temperature from Data Link | 1 C / bit | -40 C | -40 to 210 C | J1939 Temperature 1 | 78 | 4E | 0x004E
Engine Turbocharger Compressor Bypass Actuator 1 Position | R | 80 | 0x004F | 1 | Position percentage of the turbocharger compressor bypass actuator where 0% represents fully closed and 100% represents bypass fully open. | 0.4 % / bit | 0% | 0 to 100% | J1939 Percent 2 | 79 | 4F | 0x004F
Engine Turbo Charger Boost Pressure | R | 81 | 0x0050 | 1 | Gauge pressure of air measured downstream on the compressor discharge side of the turbocharger, as received from another module on the Data Link (See Register #249 for alternate source.) | 0.125 kPa / bit | 0 kPa | 0 to 8031.875 kPa | J1939 Pressure 5 | 80 | 50 | 0x0050
Intake Manifold #1 Absolute Pressure from Data Link | R | 82 | 0x0051 | 1 | Absolute air pressure of the intake manifold (instance #1), as receieved from another module on the Data Link. | 1.0 kg / hr / bit | 0 kPa | 0 to 500 kPa | J1939 Pressure 7 | 81 | 51 | 0x0051
Engine Intake Manifold #1 Absolute Pressure (High Res) | R | 83 | 0x0052 | 1 | Absolute pressure measurement of the air intake manifold, as received from another module on the Data Link. | 0.1 kPa / bit | 0 kPa | 0 to 6425.5 kPa | J1939 Pressure 3 Actual | 82 | 52 | 0x0052
Engine Inlet Air Mass Flow Rate | R | 84 | 0x0053 | 1 | Mass flow rate of fresh air entering the engine air intake, before any EGR mixer, if used. Flow rate of fresh air conducted to the engine cylinders to support combustion. | 0.05 kg/h per bit | 0 kg/h | 0 to 3212.75 kg/h | J1939 Flow Rate Mass | 83 | 53 | 0x0053
Engine Pre-filter Oil Pressure from Data Link | R | 85 | 0x0054 | 1 | Gage pressure of the engine oil before the oil reaches the oil filter, as received from another module on the Data Link. | 4 kPa / bit | 0 kPa | 0 to 1000 kPa | J1939 Pressure 1 | 84 | 54 | 0x0054
Utility Average Line-Line AC RMS Voltage Percent | R | 86 | 0x0055 | 1 | Average Line to Line RMS voltage percent measured at the utility | 0.0078125 % / bit | -251 % | -251 to 250.99 % | Percent | 85 | 55 | 0x0055
Utility Average AC RMS Frequency | R | 87 | 0x0056 | 1 | Average AC frequency measured at the Utility. | 1 V / bit | 0 V | 0 to 64255 V | AC RMS Voltage | 86 | 56 | 0x0056
Utility Average Line-Line AC RMS Voltage | R | 88 | 0x0057 | 1 | Average Line to Line RMS voltage measured at the utility | 1/128 Hz / bit | 0 Hz | 0 to 501.9922 Hz | AC Frequency | 87 | 57 | 0x0057
Number of Crank Attempts | R | 89 | 0x0058 | 2 | Accumulated number of crank attempts made by the engine. | 1 / bit | 0 | 0 to 4211081215 | Count 32 | 88 | 58 | 0x0058
Number of Successful Starts | R | 91 | 0x005A | 2 | Accumulated number of successful starts of the engine. | 1 / bit | 0 | 0 to 4211081215 | Count 32 | 90 | 5A | 0x005A
Service Maintenance Interval Hours Remaining | R | 93 | 0x005C | 1 | Maximum time in operation until the next service inspection is required. This number is negative if a service inspection is overdue. | 1 hr / bit | -32127 hr | -32127 to 32128 hr | J1939 Time Hours 2 Byte | 92 | 5C | 0x005C
Service Maintenance Interval Weeks Remaining | R | 94 | 0x005D | 1 | The number of full calendar days until the next service inspection is required. This number is negative if a service inspection is overdue. | 1 day / bit | -32127 days | -32127 to 32128 days | J1939 Calendar Weeks | 93 | 5D | 0x005D
Cooldown Duration Remaining | R | 95 | 0x005E | 1 | Time remaining in cooldown until engine is stopped. This value is only meaningful while the engine is in the Cooldown state. | 1 second / bit | 0 seconds | 0 to 64255 seconds | J1939 Time 4 | 94 | 5E | 0x005E
Generator Circuit Breaker Status | R | 96 | 0x005F | 1 | Shows the status of the Generator Circuit Breaker | 000 = OPEN 001 = CLOSED 010 = LOCKED OUT 011 = NOT AVAILABLE 100 = NOT INSTALLED |  |  | Breaker Status | 95 | 5F | 0x005F
Utility Circuit Breaker Status | R | 97 | 0x0060 | 1 | Shows the status of the Utility Circuit Breaker | 000 = OPEN 001 = CLOSED 010 = LOCKED OUT 011 = NOT AVAILABLE 100 = NOT INSTALLED |  |  | Breaker Status | 96 | 60 | 0x0060
SCADA Alarm Group #1 | R | 101 | 0x0064 | 1 | SCADA Alarm Group #1 | Bit 15 = Event 16 active Status Bit 14 = Event 15 active Status Bit 13 = Event 14 active Status Bit 12 = Event 13 active Status Bit 11 = Event 12 active Status Bit 10 = Event 11 active Status Bit 9 = Event 10 active Status Bit 8 = Event 9 active Status Bit 7 = Event 8 active Status Bit 6 = Event 7 active Status Bit 5 = Event 6 active Status Bit 4 = Event 5 active Status Bit 3 = Event 4 active Status Bit 2 = Event 3 active Status Bit 1 = Event 2 active Status Bit 0 = Event 1 active Status | 0= not active 1= active |  | SCADA ALARM GROUP EVENTS | 100 | 64 | 0x0064
SCADA Alarm Group #2 | R | 102 | 0x0065 | 1 | SCADA Alarm Group #2 | Bit 15 = Event 16 active Status Bit 14 = Event 15 active Status Bit 13 = Event 14 active Status Bit 12 = Event 13 active Status Bit 11 = Event 12 active Status Bit 10 = Event 11 active Status Bit 9 = Event 10 active Status Bit 8 = Event 9 active Status Bit 7 = Event 8 active Status Bit 6 = Event 7 active Status Bit 5 = Event 6 active Status Bit 4 = Event 5 active Status Bit 3 = Event 4 active Status Bit 2 = Event 3 active Status Bit 1 = Event 2 active Status Bit 0 = Event 1 active Status | 0= not active 1= active |  | SCADA ALARM GROUP EVENTS | 101 | 65 | 0x0065
SCADA Alarm Group #3 | R | 103 | 0x0066 | 1 | SCADA Alarm Group #3 | Bit 15 = Event 16 active Status Bit 14 = Event 15 active Status Bit 13 = Event 14 active Status Bit 12 = Event 13 active Status Bit 11 = Event 12 active Status Bit 10 = Event 11 active Status Bit 9 = Event 10 active Status Bit 8 = Event 9 active Status Bit 7 = Event 8 active Status Bit 6 = Event 7 active Status Bit 5 = Event 6 active Status Bit 4 = Event 5 active Status Bit 3 = Event 4 active Status Bit 2 = Event 3 active Status Bit 1 = Event 2 active Status Bit 0 = Event 1 active Status | 0= not active 1= active |  | SCADA ALARM GROUP EVENTS | 102 | 66 | 0x0066
SCADA Alarm Group #4 | R | 104 | 0x0067 | 1 | SCADA Alarm Group #4 | Bit 16 = Event 16 active Status Bit 15 = Event 15 active Status Bit 14 = Event 14 active Status Bit 13 = Event 13 active Status Bit 12 = Event 12 active Status Bit 11 = Event 11 active Status Bit 10 = Event 10 active Status Bit 9 = Event 9 active Status Bit 8 = Event 8 active Status Bit 7 = Event 7 active Status Bit 6 = Event 6 active Status Bit 5 = Event 5 active Status Bit 4 = Event 4 active Status Bit 3 = Event 3 active Status Bit 2 = Event 2 active Status Bit 1 = Event 1 active Status | 0= not active 1= active |  | SCADA ALARM GROUP EVENTS | 103 | 67 | 0x0067
SCADA Alarm Group #5 | R | 105 | 0x0068 | 1 | SCADA Alarm Group #5 | Bit 15 = Event 16 active Status Bit 14 = Event 15 active Status Bit 13 = Event 14 active Status Bit 12 = Event 13 active Status Bit 11 = Event 12 active Status Bit 10 = Event 11 active Status Bit 9 = Event 10 active Status Bit 8 = Event 9 active Status Bit 7 = Event 8 active Status Bit 6 = Event 7 active Status Bit 5 = Event 6 active Status Bit 4 = Event 5 active Status Bit 3 = Event 4 active Status Bit 2 = Event 3 active Status Bit 1 = Event 2 active Status Bit 0 = Event 1 active Status | 0= not active 1= active |  | SCADA ALARM GROUP EVENTS | 104 | 68 | 0x0068
SCADA Alarm Group #6 | R | 106 | 0x0069 | 1 | SCADA Alarm Group #6 | Bit 15 = Event 16 active Status Bit 14 = Event 15 active Status Bit 13 = Event 14 active Status Bit 12 = Event 13 active Status Bit 11 = Event 12 active Status Bit 10 = Event 11 active Status Bit 9 = Event 10 active Status Bit 8 = Event 9 active Status Bit 7 = Event 8 active Status Bit 6 = Event 7 active Status Bit 5 = Event 6 active Status Bit 4 = Event 5 active Status Bit 3 = Event 4 active Status Bit 2 = Event 3 active Status Bit 1 = Event 2 active Status Bit 0 = Event 1 active Status | 0= not active 1= active |  | SCADA ALARM GROUP EVENTS | 105 | 69 | 0x0069
SCADA Alarm Group #7 | R | 107 | 0x006A | 1 | SCADA Alarm Group #7 | Bit 15 = Event 16 active Status Bit 14 = Event 15 active Status Bit 13 = Event 14 active Status Bit 12 = Event 13 active Status Bit 11 = Event 12 active Status Bit 10 = Event 11 active Status Bit 9 = Event 10 active Status Bit 8 = Event 9 active Status Bit 7 = Event 8 active Status Bit 6 = Event 7 active Status Bit 5 = Event 6 active Status Bit 4 = Event 5 active Status Bit 3 = Event 4 active Status Bit 2 = Event 3 active Status Bit 1 = Event 2 active Status Bit 0 = Event 1 active Status | 0= not active 1= active |  | SCADA ALARM GROUP EVENTS | 106 | 6A | 0x006A
SCADA Alarm Group #8 | R | 108 | 0x006B | 1 | SCADA Alarm Group #8 | Bit 16 = Event 16 active Status Bit 15 = Event 15 active Status Bit 14 = Event 14 active Status Bit 13 = Event 13 active Status Bit 12 = Event 12 active Status Bit 11 = Event 11 active Status Bit 10 = Event 10 active Status Bit 9 = Event 9 active Status Bit 8 = Event 8 active Status Bit 7 = Event 7 active Status Bit 6 = Event 6 active Status Bit 5 = Event 5 active Status Bit 4 = Event 4 active Status Bit 3 = Event 3 active Status Bit 2 = Event 2 active Status Bit 1 = Event 1 active Status | 0= not active 1= active |  | SCADA ALARM GROUP EVENTS | 107 | 6B | 0x006B
SCADA Alarm Group #9 | R | 109 | 0x006C | 1 | SCADA Alarm Group #9 | Bit 15 = Event 16 active Status Bit 14 = Event 15 active Status Bit 13 = Event 14 active Status Bit 12 = Event 13 active Status Bit 11 = Event 12 active Status Bit 10 = Event 11 active Status Bit 9 = Event 10 active Status Bit 8 = Event 9 active Status Bit 7 = Event 8 active Status Bit 6 = Event 7 active Status Bit 5 = Event 6 active Status Bit 4 = Event 5 active Status Bit 3 = Event 4 active Status Bit 2 = Event 3 active Status Bit 1 = Event 2 active Status Bit 0 = Event 1 active Status | 0= not active 1= active |  | SCADA ALARM GROUP EVENTS | 108 | 6C | 0x006C
SCADA Alarm Group #10 | R | 110 | 0x006D | 1 | SCADA Alarm Group #10 | Bit 15 = Event 16 active Status Bit 14 = Event 15 active Status Bit 13 = Event 14 active Status Bit 12 = Event 13 active Status Bit 11 = Event 12 active Status Bit 10 = Event 11 active Status Bit 9 = Event 10 active Status Bit 8 = Event 9 active Status Bit 7 = Event 8 active Status Bit 6 = Event 7 active Status Bit 5 = Event 6 active Status Bit 4 = Event 5 active Status Bit 3 = Event 4 active Status Bit 2 = Event 3 active Status Bit 1 = Event 2 active Status Bit 0 = Event 1 active Status | 0= not active 1= active |  | SCADA ALARM GROUP EVENTS | 109 | 6D | 0x006D
Fuel Level- final | R | 151 | 0x0096 | 1 | fuel level, independent of source. I/o pin (if configured) takes precedence over datalink. | 0.0078125 % / bit | -251 % | -251 to 250.99 % | Percent | 150 | 96 | 0x0096
Auto Start Stop State | R | 153 | 0x0098 | 1 | Current state of the Automatic Start/Stop sequence. Either read from engine (if Engine ECM controls start/stop) or determined by Genset Control. | 0 = INIT 1 = PRE CRANK 2 = STARTING 3 = RUNNING 4 = PRE COOLDOWN 5 = COOLDOWN 6 = STOPPING 7 = STOPPED 8 = IDLING 9 = WAITING TO START [only used when executing the Crank Arbitration feature] 10 = WARMING UP [only used when executing APCDL Genset Warm up feature conditions are met] |  |  | Engine Control State | 152 | 98 | 0x0098
Engine Operating Hours | R | 154 | 0x0099 | 2 | Accumulated time that the engine is running. | 0.05 hour / bit | 0 hr | 0 to 210554060.75 hour | J1939 Time 10 | 153 | 99 | 0x0099
Engine Coolant Temperature | R | 156 | 0x009B | 1 | Temperature of liquid found in engine cooling system. | 0.03125 C / bit | -273 C | -273 to 1735 C | J1939 Temperature 2 | 155 | 9B | 0x009B
Engine Operating Mode | R | 157 | 0x009C | 1 | Indicates current position of the Engine Control Switch. | 0 = STOP 1 = AUTO 2 = RUN |  |  | Engine Operating Mode | 156 | 9C | 0x009C
Engine Oil Pressure | R | 158 | 0x009D | 1 | Gauge pressure of oil in engine lubrication system as provided by oil pump. | 0.125 kPa / bit | 0 | 0 to 8031.875 kPa | J1939 Pressure 5 | 157 | 9D | 0x009D
Engine Speed | R | 159 | 0x009E | 1 | Engine rotational speed calculated in revolutions per minute. | 0.125 rpm / bit | 0 | 0 to 8031.875 rpm | J1939 Rot Vel 1 | 158 | 9E | 0x009E
Battery Voltage Monitor | R | 160 | 0x009F | 1 | Shows the Battery Voltage, as read at the input to the Genset Control. | 0.05 V / bit | 0 | 0 to 3212.75 V | J1939 Electrical Potential | 159 | 9F | 0x009F
Cooldown Duration Remaining | R | 161 | 0x00A0 | 1 | Time remaining in cooldown until engine is stopped. This value is only meaningful while the engine is in the Cooldown state. | 1 second / bit | 0 seconds | 0 to 64255 seconds | J1939 Time 4 | 160 | A0 | 0x00A0
Phase A Winding Temp | R | 162 | 0x00A1 | 1 | Temperature of the Phase A winding inside the alternator. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 161 | A1 | 0x00A1
Phase B Winding Temp | R | 163 | 0x00A2 | 1 | Temperature of the Phase B winding inside the alternator. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 162 | A2 | 0x00A2
Phase C Winding Temp | R | 164 | 0x00A3 | 1 | Temperature of the Phase C winding inside the alternator. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 163 | A3 | 0x00A3
Generator Front Bearing Temperature | R | 165 | 0x00A4 | 1 | Temperature of the bearing inside the alternator. This is the right or front bearing. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 164 | A4 | 0x00A4
Generator Rear Bearing Temperature | R | 166 | 0x00A5 | 1 | Temperature of the bearing inside the alternator. This is the left or rear bearing. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 165 | A5 | 0x00A5
Number of Engine Cylinders | R | 206 | 0x00CD | 1 | Number of engine cylinders. | 1 / bit | 0 | 0 to 65535 | Count 16 | 205 | CD | 0x00CD
Number of Crank Attempts | R | 207 | 0x00CE | 2 | Accumulated number of crank attempts made by the engine. | 1 / bit | 0 | 0 to 4211081215 | Count 32 | 206 | CE | 0x00CE
Number of Successful Starts | R | 209 | 0x00D0 | 2 | Accumulated number of successful starts of the engine. | 1 / bit | 0 | 0 to 4211081215 | Count 32 | 208 | D0 | 0x00D0
Service Maintenance Interval Hours Remaining | R | 211 | 0x00D2 | 1 | Maximum time in operation until the next service inspection is required. This number is negative if a service inspection is overdue. | 1 hr / bit | -32127 hr | -32127 to 32128 hr | J1939 Time Hours 2 Byte | 210 | D2 | 0x00D2
Service Maintenance Interval Days Remaining | R | 212 | 0x00D3 | 1 | Maximum calendar days until the next service inspection is required. This number is negative if a service inspection is overdue. | 1 day / bit | -32127 days | -32127 to 32128 days | J1939 Time Days | 211 | D3 | 0x00D3
Service Maintenance Interval Weeks Remaining | R | 213 | 0x00D4 | 1 | The number of full calendar weeks until the next service inspection is required. This number is negative if a service inspection is overdue. | 1 week / bit | -125 | -125 to 125 weeks | J1939 Calendar Weeks | 212 | D4 | 0x00D4
Engine Oil Temperature | R | 214 | 0x00D5 | 1 | Oil temp, independent of source. I/o pin (if configured) takes precedence over datalink. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 213 | D5 | 0x00D5
Engine Fuel Temperature from Data Link | R | 215 | 0x00D6 | 1 | Temperature of the engine fuel as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 214 | D6 | 0x00D6
Exhaust Manifold #1 Temperature from Data Link | R | 216 | 0x00D7 | 1 | Temperature of combustion byproducts within the left engine exhaust manifold, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 215 | D7 | 0x00D7
Exhaust Manifold #2 Temperature from Data Link | R | 217 | 0x00D8 | 1 | Temperature of combustion byproducts within the right engine exhaust manifold, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 216 | D8 | 0x00D8
Intake Manifold #1 Temperature from Data Link | R | 218 | 0x00D9 | 1 | Temperature of pre-combustion air found in intake manifold #1 of engine air supply system, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 217 | D9 | 0x00D9
Engine Oil to Engine Coolant Differential Temperature | R | 219 | 0x00DA | 1 | Engine Oil Temperature minus the Engine Coolant Temperature, as received from another module on the Data Link. | 1.0 C / bit | -273 | -273 to 32767 C | CDL Temperature 1 | 218 | DA | 0x00DA
Engine Coolant Temperature 2 | R | 220 | 0x00DB | 1 | Second temperature of liquid found in the engine cooling system | 1 C / bit | -40 | -40 to 210 C | J1939 Temperature 1 | 219 | DB | 0x00DB
Engine Coolant Temperature 3 | R | 221 | 0x00DC | 1 | Third temperature of liquid found in the engine cooling system | 1 C / bit | -40 | -40 to 210 C | J1939 Temperature 1 | 220 | DC | 0x00DC
Compressor Inlet Air Temperature from Data Link | R | 222 | 0x00DD | 1 | Temperature of air entering vehicle air induction system | 1 C / bit | -40 | -40 to 210 C | J1939 Temperature 1 | 221 | DD | 0x00DD
Engine Aftercooler Inlet Temperature from Data Link | R | 223 | 0x00DE | 1 | Engine Aftercooler Inlet Temperature from Data Link | 1 C / bit | -40 | -40 to 210 C | J1939 Temperature 1 | 222 | DE | 0x00DE
Engine Aftercooler Outlet Temperature from Data Link | R | 224 | 0x00DF | 1 | Engine Aftercooler Outlet Temperature from Data Link | 1 C / bit | -40 | -40 to 210 C | J1939 Temperature 1 | 223 | DF | 0x00DF
Auxiliary Temperature #1 from Data Link | R | 225 | 0x00E0 | 1 | Auxiliary Temperature #1 from Data Link | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 224 | E0 | 0x00E0
Auxiliary Temperature #2 from Data Link | R | 226 | 0x00E1 | 1 | Auxiliary Temperature #2 from Data Link | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 225 | E1 | 0x00E1
Fuel Pressure | R | 227 | 0x00E2 | 1 | Gauge pressure of fuel in system as delivered from supply pump to the injection pump, as received from another module on the CAN Data Link. | 0.125 kPa / bit | 0 | 0 to 8031.875 kPa | J1939 Pressure 5 | 226 | E2 | 0x00E2
Crankcase Pressure from Data Link | R | 228 | 0x00E3 | 1 | Gauge pressure inside engine crankcase, as received from another module on the CAN Data Link. | 1 / 128 kPa / bit | -250 | -250 to 251.99 kPa | J1939 Pressure 3 | 227 | E3 | 0x00E3
Boost Pressure from Data Link | R | 229 | 0x00E4 | 1 | Gauge pressure of air measured downstream on the compressor discharge side of the turbocharger, as received from another module on the CAN Data Link. | 0.125 kPa / bit | 0 | 0 to 8031.875 kPa | J1939 Pressure 5 | 228 | E4 | 0x00E4
Atmospheric Pressure from Data Link | R | 230 | 0x00E5 | 1 | Absolute air pressure of the atmosphere, as received from another module on the CAN Data Link. | 0.125 kPa / bit | 0 | 0 to 8031.875 kPa | J1939 Pressure 5 | 229 | E5 | 0x00E5
Engine Coolant Pressure from Data Link | R | 231 | 0x00E6 | 1 | Pressure of liquid found in engine cooling system (instance #1) , as received from another module on the CAN Data Link. . | 0.125 kPa / bit | 0 | 0 to 8031.875 kPa | J1939 Pressure 5 | 230 | E6 | 0x00E6
Engine Intake Manifold #1 Absolute Pressure (High Res) | R | 232 | 0x00E7 | 1 | Absolute pressure measurement of the air intake manifold, as received from another module on the Data Link. | 0.1 kPa / bit | 0 | 0 to 6425.5 kPa | J1939 Pressure 3 Actual | 231 | E7 | 0x00E7
Intake Manifold #1 Absolute Pressure from Data Link | R | 233 | 0x00E8 | 1 | Absolute air pressure of the intake manifold (instance #1), as receieved from another module on the Data Link. | 2 kPa / bit | 0 | 0 to 500 kPa | J1939 Pressure 7 | 232 | E8 | 0x00E8
Engine Air to Fuel Differential Pressure | R | 234 | 0x00E9 | 1 | The differential pressure between the gaseous fuel and the air intake manifold. | 0.1 kPa / bit | 0 | 0 to 6425.5 kPa | J1939 Pressure 3 Actual | 233 | E9 | 0x00E9
Engine Turbo Charger Boost Pressure | R | 235 | 0x00EA | 1 | Gauge pressure of air measured downstream on the compressor discharge side of the turbocharger, as received from another module on the Data Link (See Register #249 for alternate source.) | 0.125 kPa / bit | 0 | 0 to 8031.875 kPa | J1939 Pressure 5 | 234 | EA | 0x00EA
Engine Air Filter #2 Differential Pressure | R | 236 | 0x00EB | 1 | Engine Air Filter #2 Differential Pressure | 0.05 kPa / bit | 0 | 0 to 12.5 kPa | J1939 Pressure 8 | 235 | EB | 0x00EB
Engine Fuel Valve Differential Pressure | R | 237 | 0x00EC | 1 | Differential pressure between the intake and the outlet of a gaseous fuel valve, as received from another module on the Data Link. | 0.1 kPa / bit | 0 | 0 to 6425.5 kPa | J1939 Pressure 3 Actual | 236 | EC | 0x00EC
Engine Turbocharger Compressor Control | R | 238 | 0x00ED | 1 | Command to a compressor bypass actuator, normalized to percent, where 0% nominally represents fully closed and 100% represents fully open, as received from another module on the Data Link. | 0.0025 % / bit | 0 | 0 to 160.6375 % | J1939 Percent 1 | 237 | ED | 0x00ED
Engine Turbocharger Compressor Bypass Actuator 1 Position | R | 239 | 0x00EE | 1 | Position percentage of the turbocharger compressor bypass actuator where 0% represents fully closed and 100% represents bypass fully open. | 0.4 % / bit | 0 | 0 to 100% | J1939 Percent 2 | 238 | EE | 0x00EE
Left Turbo Inlet Pressure from Data Link | R | 240 | 0x00EF | 1 | Gage pressure of the air entering the compressor side of the turbocharger from Data Link | 1 / 128 kPa / bit | -250 | -250 to 251.99 kPa | J1939 Pressure 3 | 239 | EF | 0x00EF
Right Turbo Inlet Pressure from Data Link | R | 241 | 0x00F0 | 1 | Gage pressure of the air entering the compressor side of the turbocharger from Data Link | 1 / 128 kPa / bit | -250 | -250 to 251.99 kPa | J1939 Pressure 3 | 240 | F0 | 0x00F0
Engine Throttle Valve Differential Pressure - CONFIRM SPN DEFINITION | R | 242 | 0x00F1 | 1 | Differential pressure between the intake and outlet of the engine throttle valve, as received from another module on the Data Link. | 0.1 kPa / bit | 0 | 0 to 6425.5 kPa | J1939 Pressure 3 Actual | 241 | F1 | 0x00F1
Desired Engine Throttle Valve Differential Pressure | R | 243 | 0x00F2 | 1 | Desired pressure differential across the engine throttle valve, as received from another module on the Data Link. | 0.1 kPa / bit | 0 | 0 to 6550.3 kPa | CDL Pressure 1 | 242 | F2 | 0x00F2
Hydraulic Pressure | R | 244 | 0x00F3 | 1 | Hydraulic Pressure measured at the output of Hydraulic pump | 2kPA / bit | 0 | 0 to 128,510 | J1939 Pressure 14 | 243 | F3 | 0x00F3
Oil Filter Differential Pressure from Data Link | R | 245 | 0x00F4 | 1 | Change in engine oil pressure, measured across the filter, due to the filter and any accumulation of solid or semisolid material on or in the filter, as received from another module on the CAN Data Link. | 0.125 kPa / bit | 0 | 0 to 8031.875 kPa | J1939 Pressure 5 | 244 | F4 | 0x00F4
Fuel Filter Differential Pressure from Data Link | R | 246 | 0x00F5 | 1 | Change in fuel delivery pressure, measured across the filter, due to accumulation of solid or semisolid matter on the filter element, as received from another module on the CAN Data Link. | 0.125 kPa / bit | 0 | 0 to 8031.875 kPa | J1939 Pressure 5 | 245 | F5 | 0x00F5
Air Filter 1 Differential Pressure from Data Link | R | 247 | 0x00F6 | 1 | Change in engine air system pressure, measured across the filter, due to the filter and any accumulation of solid foreign matter on or in the filter, as received from another module on the CAN Data Link. | 1 / 128 kPa / bit | -250 | -250 to 251.99 kPa | J1939 Pressure 3 | 246 | F6 | 0x00F6
Engine Pre-filter Oil Pressure from Data Link | R | 248 | 0x00F7 | 1 | Gage pressure of the engine oil before the oil reaches the oil filter, as received from another module on the Data Link. | 4 kPa / bit | 0 | 0 to 1000 kPa | J1939 Pressure 1 | 247 | F7 | 0x00F7
Instantaneous Fuel Consumption from Data Link | R | 249 | 0x00F8 | 1 | Amount of fuel used by engine per unit time, as received from another module on the CAN Data Link. | 0.05 L/h per bit | 0 | 0 to 3212.75 L/h | J1939 Flow Rate Liquid | 248 | F8 | 0x00F8
Total Fuel Consumption from Data Link | R | 250 | 0x00F9 | 2 | Total amount of fuel used by engine, as received from another module on the CAN Data Link. | 0.5 L / bit | 0 L | 0 to 2105540607.5 L | J1939 Volume | 249 | F9 | 0x00F9
Fuild Bund Level | R | 252 | 0x00FB | 1 | Indicates the fluid bund level percentage | 0.0078125 % / bit | -251 % | -251 to 250.99 % | Percent | 251 | FB | 0x00FB
Fuel Level | R | 253 | 0x00FC | 1 | Fuel level, as read from i/o pin. | 0.0078125 % / bit | -251 % | -251 to 250.99 % | Percent | 252 | FC | 0x00FC
Fuel Energy Content | R | 254 | 0x00FD | 1 | Energy content (lower heating value) of the gaseous fuel, as received from another module on the Data Link. | 1 / 256 MJ / Nm^3 per bit | 0 | 0 to 250.996 MJ / Nm^3 | J1939 Fuel Energy Content | 253 | FD | 0x00FD
Engine Gaseous Fuel Correction Factor | R | 255 | 0x00FE | 1 | A correction to a predefined gaseous fuel energy content represented as a percentage, as received from another module on the Data Link. (Actual fuel energy used is the product of gasueous fuel correction factor and the energy of the gas) | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 254 | FE | 0x00FE
Engine Fuel Specific Gravity | R | 256 | 0x00FF | 1 | Measured specific gravilty of the fuel, as received from another module on the Data Link. | 0.0001 / bit | 0 | 0 to 6.4255 | J1939 Specific Gravity | 255 | FF | 0x00FF
Specific Heat Ratio | R | 257 | 0x00100 | 1 | Measured specific heat ratio of the fuel, as received from another module on the Data Link. | 0.001 / bit | 0 | 0 to 64.255 | J1939 Specific Heat | 256 | 100 | 0x00100
Engine Percent Load At Current Speed | R | 258 | 0x00101 | 1 | Percentage that represents the ratio of actual engine percent torque to maximum indicated torque available at the current engine speed, as received from another module on the Data Link. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 257 | 101 | 0x00101
Engine Inlet Air Mass Flow Rate | R | 259 | 0x00102 | 1 | Mass flow rate of fresh air entering the engine air intake, before any EGR mixer, if used. Flow rate of fresh air conducted to the engine cylinders to support combustion. | 0.05 kg/h per bit | 0 | 0 to 3212.75 kg/h | J1939 Flow Rate Mass | 258 | 102 | 0x00102
Fuel Valve 1 Inlet Absolute Pressure from Data Link | R | 260 | 0x00103 | 1 | Absolute pressure of gas on the intake side of the first system control valve, as received from another module on the Data Link. | 0.1 kPa / bit | 0 | 0 to 6425.5 kPa | J1939 Pressure 3 Actual | 259 | 103 | 0x00103
Engine Throttle Actuator #1 Control Command | R | 261 | 0x00104 | 1 | Control command to throttle actuator (instance #1), normalized to percent, where 0% represents fully closed and 100% represents fully open, as received from another module on the Data Link. | 0.0025 % / bit | 0 | 0 to 160.6375 % | J1939 Percent 1 | 260 | 104 | 0x00104
Actual Maximum Available Engine -Percent Fuel | R | 262 | 0x00105 | 1 | Indicates the percent of torque limited fuel relative to the engine standard torque fuel. | 0.4 % / bit | 0 | 0 to 100% | J1939 Percent 2 | 261 | 105 | 0x00105
Urea Tank Level | R | 263 | 0x00106 | 1 | SCR urea tank level, as read from the CAN Data Link. | 0.4 % / bit | 0 | 0 to 100% | J1939 Percent 2 | 262 | 106 | 0x00106
Aftertreatment #1 SCR Catalyst Reagent Tank #1 Temperature | R | 264 | 0x00107 | 1 | SCR catalyst tank temperature, as read from the CAN Data Link. | 1 C / bit | -40 | -40 to 210 C | J1939 Temperature 1 | 263 | 107 | 0x00107
Urea Injection Air Supply Pressure | R | 265 | 0x00108 | 1 | SCR urea injection air pressure, as read from the CAN Data Link. | 0.1 kPa / bit | 0 | 0 to 6425.5 kPa | J1939 Pressure 3 Actual | 264 | 108 | 0x00108
Catalyst Intake Temperature | R | 266 | 0x00109 | 1 | SCR catalyst intake temperature, as read from the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 265 | 109 | 0x00109
Aftertreatment 1 SCR Catalyst Exhaust Gas Differential Pressure | R | 267 | 0x0010A | 1 | SCR catalyst exhaust diff pressure (intake to exhaust), as read from the CAN Data Link. | 0.1 kPa / bit | 0 | 0 to 6425.5 kPa | J1939 Pressure 3 Actual | 266 | 10A | 0x0010A
Aftertreatment Soot Load Level | R | 268 | 0x0010B | 1 | Percentage of soot built inside of the Diesel Particulate Filter | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 267 | 10B | 0x0010B
SCR System State | R | 269 | 0x0010C | 1 | Operating state of the SCR system, as read from the CAN Data Link | 0000 ($0) = Sleep Mode 0001 ($1) = Preparing 0010 ($2) = Normal 0011 ($3) = System Error Pending 0100 ($4) = DEF Purging 0101 ($5) = Heat Protection 0110 ($6) = Cold Protection 0111 ($7) = Shutoff 1000 ($8) = Diagnosis 1001 ($9) = Service Mode, Dose Allowed 1010 ($10) = Service Mode, Dose Not Allowed / Dose Inhibit 1011 ($11) = Ok to Power Down 1100 ($12) = Reserved for future use. 1101 ($13) = Reserved for future use. 1110 ($14) = Error 1111 ($15) = Not Available |  |  | SCR System State | 268 | 10C | 0x0010C
Aftertreatment DEF Dosing Temperature | R | 270 | 0x0010D | 1 | Diesel Exhaust Fluid Dosing Temperature, as read from the CAN Data Link. | 1 C / bit | -40 | -40 to 210 C | J1939 Temperature 1 | 269 | 10D | 0x0010D
Aftertreatment Total DEF Used | R | 271 | 0x0010E | 2 | Total amount of DEF used by aftertreatment device 1 over the lifetime of the device. | 0.5 L / bit | 0 L | 0 to 2105540607.5 L | J1939 Volume | 270 | 10E | 0x0010E
Time Since Aftertreatment Inducement | R | 273 | 0x00110 | 1 | Time since last aftertreatment inducement. | 0.2 hour / bit | 0 hours | 0 to 12851 hours | J1939 Time 8 | 272 | 110 | 0x00110
Time Until Aftertreatment Inducement | R | 274 | 0x00111 | 1 | Time remaining until next aftertreatment inducement. | 0.25 hour / bit | 0 hours | 0 to 62.5 hours | J1939 Time 9 | 273 | 111 | 0x00111
SCR Operator Inducement Override Mode | R | 275 | 0x00112 | 1 | Indicates the functional mode of SCR operator inducement override | 000 = Not Enabled 001 = Available Not Active 010 = Active 011 = Active Extended 100 = Expired 101 = Not Defined 110 = Not Defined 111 = Not Available |  |  | SCR Operator Inducement Override Mode | 274 | 112 | 0x00112
SCR Operator Inducement Override Time Remaining | R | 276 | 0x00113 | 1 | Indicate the time remaining during an operator inducement override event. | 1 minute / bit | 0 | 0 to 64255 mins | SCR Operator Inducement Override Time Remaining | 275 | 113 | 0x00113
Aftertreatment 1 SCR System Hydrocarbon | R | 277 | 0x00114 | 1 | Indicates the ratio of the mass of hydrocarbon present in the aftertreatment system compared to the maximum allowable mass of hydrocarbon for the aftertreatment system | 0.5 kPa / bit | 0 kPa |  | J1939 Percent 6 | 276 | 114 | 0x00114
Gas Substitution Status | R | 278 | 0x00115 | 1 | Status of the gas substitution feature. | 00 = Inactive 01 = Active 10 = Locked Inactive |  |  | Gas Substitution Status | 277 | 115 | 0x00115
Maximum Gas Substitution Percentage | R | 279 | 0x00116 | 1 | Maximum gas substitution as a percentage of the maximum gas-to- diesel fuel substitution rate (0% = No substitution of gas - full diesel,100% = Maximum gas-to-diesel substitution requested). | 0.0078125 % / bit | -251 % | -251 to 250.99 % | Percent | 278 | 116 | 0x00116
Gas Substitution Reduction Reason | R | 280 | 0x00117 | 1 | Indicates the reason gas substitution mode is not at the requested level. | 0 - NONE 1- DIAG ACTIVE 2- LOW LOAD 3 - HI TURBO TEMP 4 - HI DET LVL 5 - HI VALVE CMD |  |  | Gas Substitution Reduction Reason | 279 | 117 | 0x00117
Actual Gas Substitution Percentage | R | 281 | 0x00118 | 1 | Actual power, as percentage of maximum power, provided by gas to substitute diesel power. | 0.0078125 % / bit | -251 % | -251 to 250.99 % | Percent | 280 | 118 | 0x00118
Fuel Shutoff 1 Control from Data Link | R | 282 | 0x00119 | 1 | Fuel control setting for fuel shutoff (instance #1), as received from another module on the Data Link. | 0 = OPEN 1 = CLOSED 2 = LOCKED OUT 7 = ERROR |  |  | Breaker Status | 281 | 119 | 0x00119
Total Fuel Used without Gas Substitution | R | 283 | 0x0011A | 2 | Accumulated amount of liquid fuel that would have been used during engine operation, including actual diesel fuel used and the diesel fuel that was displaced by gaseous fuel. | 0.5 L / bit | 0 L | 0 to 2105540607.5 L | J1939 Volume | 282 | 11A | 0x0011A
Fuel Consumption Rate without Gas Substitution | R | 285 | 0x0011C | 1 | Indicates the amount of diesel fuel that would be consumed by an engine per unit of time if it were not substituting gaseous fuel. | 0.05 L/h per bit | 0 L/h | 0 to 3212.75 L/h | J1939 Flow Rate Liquid | 284 | 11C | 0x0011C
Resettable Fuel Used | R | 286 | 0x0011D | 2 | Indicates the fuel used. This is a resettable total, and not a lifetime total | 0.125 Gal/bit | 0 | 0 to 536870907.87 Gal | CDL Gallons | 285 | 11D | 0x0011D
Resettable Equivalent Fuel Used Without Gas Substitution | R | 288 | 0x0011F | 2 | Indicates the total equivalent quantity of diesel fuel that would have been consumed by the engine if gaseous fuel had not been substituted for a portion of the diesel fuel | 0.125 Gal/bit | 0 | 0 to 536870907.87 Gal | CDL Gallons | 287 | 11F | 0x0011F
Desired Ignition Timing | R | 290 | 0x00121 | 1 | Desired ignition timing value specific to engine application, as received from engine ECM on the Data Link. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 289 | 121 | 0x00121
Engine Actual Ignition Timing | R | 291 | 0x00122 | 1 | Actual ignition timing at the current engine conditions, as received from another module on the Data Link. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 290 | 122 | 0x00122
Engine Fuel Valve #1 Position | R | 292 | 0x00123 | 1 | Position of a gaseous fuel valve (instance #1) that is metering the fuel flow to the engine, as received from another module on the Data Link. 0% indicates no fuel flow through valve and 100% indicates maximum fuel flow through valve. | 0.4 % / bit | 0 | 0 to 100% | J1939 Percent 2 | 291 | 123 | 0x00123
Requested Engine Fuel Valve #1 Position | R | 293 | 0x00124 | 1 | Requested position of a gaseous fuel valve (instance #1) that is metering the fuel flow to the engine, as received from another module on the Data Link. | 0.4 % / bit | 0 | 0 to 100% | J1939 Percent 2 | 292 | 124 | 0x00124
Engine Throttle Valve Position | R | 294 | 0x00125 | 1 | Read the actual position (as a percentage of full supply) of the valve used to regulate the supply of a fluid (usually air or fuel/air mixture) to the engine, as received from another module on the Data Link. | 0.4 % / bit | 0 | 0 to 100% | J1939 Percent 2 | 293 | 125 | 0x00125
Desired Engine Throttle Valve Position | R | 295 | 0x00126 | 1 | Read the desired position (as a percentage of full supply) of the Throttle valve (instance #1) that is regulating the fluid (usually air/fuel mixture) to the engine, as received from another module on the Data Link. | 0.4 % / bit | 0 | 0 to 100% | J1939 Percent 2 | 294 | 126 | 0x00126
Emissions Feedback Mode | R | 296 | 0x00127 | 1 | Used to read the current feedback method/mode for emissions control. | 394 = Combustion Time (CT) 395 = Exhaust Temperature (EXH TEMP) 396 = Oxygen (OXYGEN) 397 = Calibration (CALIBRATE) 398 = No Feedback (DISABLED) 938 = Charge Density (CD) 995 = NOx (NOx) 1003 = Disabled (DISABLED) |  |  | Emissions Feedback Mode | 295 | 127 | 0x00127
Three Way Catalyst Intake Temperature | R | 297 | 0x00128 | 1 | Temperature of engine combustion byproducts entering the Three Way Catalyst in exhaust bank #1, as received from another module on the Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 296 | 128 | 0x00128
Three Way Catalyst Outlet Temperature | R | 298 | 0x00129 | 1 | Temperature of engine combustion byproducts leaving the Three Way Catalyst in exhaust bank #1, as received from another module on the Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 297 | 129 | 0x00129
Three Way Catalyst Differential Temperature | R | 299 | 0x0012A | 1 | Differential engine combustion byproducts gas temperature measured between the intake and outlet of the three way catalyst for exhaust bank #1, as received from another module on the Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 298 | 12A | 0x0012A
Aftertreatment Intake O2 Percent | R | 300 | 0x0012B | 1 | The actual oxidation factor (%O2) of the gas within the exhaust stream. - from Data Link | 0.05 kPa / bit | 0 | 0 to 12.5 kPa | J1939 Percent 8 | 299 | 12B | 0x0012B
Aftertreatment Outlet O2 Percent | R | 301 | 0x0012C | 1 | The actual oxidation factor (%O2) of the gas within the exhaust stream - from Data Link | 0.05 kPa / bit | 0 | 0 to 12.5 kPa | J1939 Percent 8 | 300 | 12C | 0x0012C
Oxygen Sensor Status | R | 302 | 0x0012D | 1 | Status of the oxygen sensor that reflects the output commanded by the ECM, as received from another module on the Data Link. | 0 = OFF 1 = ON |  |  | On Status | 301 | 12D | 0x0012D
Oxygen Sensor Closed Loop Operation | R | 303 | 0x0012E | 1 | Indicates whether the engine is using the Exhaust Gas Oxygen sensor to control the air/fuel ratio, as received from another module on the Data Link. | 00 = OPEN LOOP 01 = CLOSED LOOP 10 = RESERVED 11 = DON'T CARE / TAKE NO ACTION |  |  | Closed Loop Status | 302 | 12E | 0x0012E
Intake Oxygen Sensor Voltage | R | 304 | 0x0012F | 1 | Actual voltage from the Aftertreatment #1 Intake Oxygen sensor mounted at the intake of the Aftertreatment #1 system, as received from another module on the Data Link. | 0.5 mV / bit | 0 | 0 to 32127.5 mV | Electrical Voltage, mV | 303 | 12F | 0x0012F
Desired Intake Oxygen Sensor Voltage | R | 305 | 0x00130 | 1 | Desired voltage for the Aftertreatment #1 Intake Oxygen sensor mounted at the intake of the Aftertreatment #1 system, as received from another module on the Data Link. | 0.5 mV / bit | 0 | 0 to 32127.5 mV | Electrical Voltage, mV | 304 | 130 | 0x00130
Outlet Oxygen Sensor Voltage | R | 306 | 0x00131 | 1 | Actual voltage from the Aftertreatment #1 Outlet Oxygen sensor mounted at the outlet of the Aftertreatment #1 system, as received from another module on the Data Link. | 0.5 mV / bit | 0 | 0 to 32127.5 mV | Electrical Voltage, mV | 305 | 131 | 0x00131
Desired Outlet Oxygen Sensor Voltage | R | 307 | 0x00132 | 1 | Desired voltage for the Aftertreatment #1 Outlet Oxygen sensor mounted at the outlet of the Aftertreatment #1 system, as received from another module on the Data Link. | 0.5 mV / bit | 0 | 0 to 32127.5 mV | Electrical Voltage, mV | 306 | 132 | 0x00132
Intake Oxygen Sensor Fuel Trim Percentage | R | 308 | 0x00133 | 1 | Percentage adjustment made by the Aftertreatment #1 Intake Oxygen sensor to the fuel actuator control command, as received from another module on the Data Link. | 0.01 % / bit | -320 % | -320 to 322.55 % | Percent 2 | 307 | 133 | 0x00133
Outlet Oxygen Sensor Fuel Trim Percentage | R | 309 | 0x00134 | 1 | Percentage adjustment made by the Aftertreatment #1 Outlet Oxygen sensor to the fuel actuator control command, as received from another module on the Data Link. | 0.01 % / bit | -320 % | -320 to 322.55 % | Percent 2 | 308 | 134 | 0x00134
Engine Running Status | R | 310 | 0x00135 | 1 | Engine running status, as received from the engine ECM on the Data Link. True indicates the engine is running. | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 309 | 135 | 0x00135
Engine Ventilation Status | R | 311 | 0x00136 | 1 | Indicates the engine ventailation status. | 01 = TRUE |  |  | Engine Ventilation Status | 310 | 136 | 0x00136
Gas Fuel Flow | R | 312 | 0x00137 | 1 | Gas mass flow rate delivered to the engine (instance #1), as received from another module on the Data Link. | 0.05 kg/h per bit | 0 | 0 to 3212.75 kg/h | J1939 Flow Rate Mass | 311 | 137 | 0x00137
Desired Air to Fuel Ratio | R | 313 | 0x00138 | 1 | Desired Air/Fuel Ratio | 0.001 / bit | 0 | 0 to 65.503 | CDL Air/Fuel Ratio 2 | 312 | 138 | 0x00138
Actual Air to Fuel Ratio | R | 314 | 0x00139 | 1 | Actual air/fuel ratio, as received from another module on the Data Link. | 0.1 / bit | 0 | 0.0 to 30.0 | CDL Air/Fuel Ratio | 313 | 139 | 0x00139
Intake Manifold Air Flow | R | 315 | 0x0013A | 1 | Used to read the flow of air through the intake manifold. | 1 SCFM / bit | 0 | 0 to 65503 SCFM | CDL Flow Rate Volume | 314 | 13A | 0x0013A
Desired Intake Manifold Air Pressure | R | 316 | 0x0013B | 1 | Used to read the desired intake manifold air pressure. | 0.1 kPa / bit | 0 | 0 to 6550.3 kPa | CDL Pressure 1 | 315 | 13B | 0x0013B
Choke Position Command | R | 317 | 0x0013C | 1 | Used to read the choke position command. This is the choke position being requested by the ECM to the actuator | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 316 | 13C | 0x0013C
Wastegate Position Command | R | 318 | 0x0013D | 1 | Used to read an engine load percentage at the current engine speed. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 317 | 13D | 0x0013D
Exhaust NOx Level | R | 319 | 0x0013E | 1 | Actual level of NOx concentration in the engine exhaust as measured by the NOx Sensor, as received from another module on the Data Link. | 0.05 ppm / bit | 0 | 0 to 3275.15 ppm | CDL NOx Level 1 | 318 | 13E | 0x0013E
Desired Exhaust NOx Level | R | 320 | 0x0013F | 1 | Desired level of NOx concentration in the engine exhaust, as received from another module on the Data Link. | 0.05 ppm / bit | 0 | 0 to 3275.15 ppm | CDL NOx Level 1 | 319 | 13F | 0x0013F
Exhaust NOx Level Sensor Status | R | 321 | 0x00140 | 1 | Status of the Engine Exhaust NOx Level Sensor, as received from another module on the Data Link. | 0 =OFF 14 = ACTIVE 15 = INACTIVE 1004 = HEATING |  |  | CDL NOx Level Sensor Status | 320 | 140 | 0x00140
Three Way Catalyst Differential Pressure | R | 322 | 0x00141 | 1 | Exhaust differential pressure measured between the intake and exhaust of a Three Way Catalyst in exhaust bank 1. | 0.1 kPa / bit | 0 kPa | 0 to 6425.5 kPa | J1939 Pressure 3 Actual | 321 | 141 | 0x00141
Engine Low Idle Switch Position | R | 323 | 0x00142 | 1 | Indicates whether the Engine is in low idle state. | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 322 | 142 | 0x00142
Engine Emergency Shutdown Indication | R | 324 | 0x00143 | 1 | Indication that the engine control system is immediately shutting the engine down | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 323 | 143 | 0x00143
Engine Auxiliary Shutdown Switch | R | 325 | 0x00144 | 1 | Switch signal which requests that all engine fueling stop. | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 324 | 144 | 0x00144
Engine Oil Priming State | R | 326 | 0x00145 | 1 | Indicates the engine is (or has recently been) sufficiently lubricated for starting purposes. | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 325 | 145 | 0x00145
Engine Oil Priming Switch | R | 327 | 0x00146 | 1 | Indicates the status of the switch input for activating the engine oil priming pump, as received from an another module on the Data Link. | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 326 | 146 | 0x00146
Starter Relay Coil Status | R | 328 | 0x00147 | 1 | Indicates status of the start relay coil | 0=NOT ENERGIZED |  |  | Starter Relay Coil Status | 327 | 147 | 0x00147
Engine Starter Mode | R | 329 | 0x00148 | 1 | Indicates the reason why an engine cannot start, as received from the engine ECM on the Data Link. | 0000 = Start Not Requested (NOT REQ) 0001 = Starter Active, Gear Not Engaged (NOT ENGAGE) 0010 = Starter Active, Gear Engaged (ENGAGED) 0011 = Start Finished, Starter Not Active (NOT ACTIVE) 0100 = Starter Inhibited, Engine Running (RUNNING) 0101 = Starter Inhibited, Engine Not Ready (NOT READY) 0110 = Starter Inhibited, Driveline Engaged (DRIVELINE) 0111 = Starter Inhibited, Active Immobilizer (IMMOBILIZER) 1000 = Starter Inhibited, Over-temp (OVER TEMP) 1001 = Starter Inhibited, Air Shutoff Valve Active (AIR SHUTOFF) 1010 = Starter Inhibited, SCR Inducement Active (SCR ACTIVE) 1011 = Reserved (RESERVED) 1100 = Starter Inhibited, Reason Unkown (UNKNOWN) 1101 = Error (legacy) (ERROR) 1110 = Error (ERROR) 1111 = Not Available (NOT AVAIL) |  |  | Engine Starter Mode | 328 | 148 | 0x00148
Engine Hydraulic Pressure Governor Switch | R | 330 | 0x00149 | 1 | Engine Hydraulic Pressure Governor Switch as received by the engine ECM | 0 = OFF 1 = ON 2 = ERROR 3 = NOT AVAILABLE |  |  | Hydraulic Pressure Switch Status | 329 | 149 | 0x00149
Engine Pre-Lube Mode | R | 331 | 0x0014A | 1 | Engine Pre-Lube Mode as received by the engine ECM | 0 = OFF 1 = ON 2 = DISABLED 3 = COMPLETE |  |  | Engine Pre-Lube Mode Status | 330 | 14A | 0x0014A
Engine Derate Percentage | R | 332 | 0x0014B | 1 | Engine derate request as received from the engine ECM | 0.4 % / bit | 0% | 0 to 100% | J1939 Percent 2 | 331 | 14B | 0x0014B
Desired Engine Speed | R | 333 | 0x0014C | 1 | Indication of the desired engine operating speed as received from the engine ECM on the CAN Data Link. | 0.125 rpm / bit | 0 rpm | 0 to 8031.875 rpm | J1939 Rot Vel 1 | 332 | 14C | 0x0014C
Cylinder #1 Exhaust Port Temperature from Data Link | R | 334 | 0x0014D | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 333 | 14D | 0x0014D
Cylinder #2 Exhaust Port Temperature from Data Link | R | 335 | 0x0014E | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 334 | 14E | 0x0014E
Cylinder #3 Exhaust Port Temperature from Data Link | R | 336 | 0x0014F | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 335 | 14F | 0x0014F
Cylinder #4 Exhaust Port Temperature from Data Link | R | 337 | 0x00150 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 336 | 150 | 0x00150
Cylinder #5 Exhaust Port Temperature from Data Link | R | 338 | 0x00151 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 337 | 151 | 0x00151
Cylinder #6 Exhaust Port Temperature from Data Link | R | 339 | 0x00152 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 338 | 152 | 0x00152
Cylinder #7 Exhaust Port Temperature from Data Link | R | 340 | 0x00153 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 339 | 153 | 0x00153
Cylinder #8 Exhaust Port Temperature from Data Link | R | 341 | 0x00154 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 340 | 154 | 0x00154
Cylinder #9 Exhaust Port Temperature from Data Link | R | 342 | 0x00155 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 341 | 155 | 0x00155
Cylinder #10 Exhaust Port Temperature from Data Link | R | 343 | 0x00156 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 342 | 156 | 0x00156
Cylinder #11 Exhaust Port Temperature from Data Link | R | 344 | 0x00157 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 343 | 157 | 0x00157
Cylinder #12 Exhaust Port Temperature from Data Link | R | 345 | 0x00158 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 344 | 158 | 0x00158
Cylinder #13 Exhaust Port Temperature from Data Link | R | 346 | 0x00159 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 345 | 159 | 0x00159
Cylinder #14 Exhaust Port Temperature from Data Link | R | 347 | 0x0015A | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 346 | 15A | 0x0015A
Cylinder #15 Exhaust Port Temperature from Data Link | R | 348 | 0x0015B | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 347 | 15B | 0x0015B
Cylinder #16 Exhaust Port Temperature from Data Link | R | 349 | 0x0015C | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 348 | 15C | 0x0015C
Cylinder #17 Exhaust Port Temperature from Data Link | R | 350 | 0x0015D | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 349 | 15D | 0x0015D
Cylinder #18 Exhaust Port Temperature from Data Link | R | 351 | 0x0015E | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 350 | 15E | 0x0015E
Cylinder #19 Exhaust Port Temperature from Data Link | R | 352 | 0x0015F | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 351 | 15F | 0x0015F
Cylinder #20 Exhaust Port Temperature from Data Link | R | 353 | 0x00160 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 352 | 160 | 0x00160
Exhaust Gas Temperature Average from Data Link | R | 354 | 0x00161 | 1 | Average temperature based upon the exhaust port temperature measurements at each of the engine cylinders, as received from another module on the Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 353 | 161 | 0x00161
Allowable Engine Cylinder Temperature High Limit from Average | R | 355 | 0x00162 | 1 | Allowable Engine Cylinder Temperature High Limit from Average | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 354 | 162 | 0x00162
Allowable Engine Cylinder Temperature Low Limit from Average | R | 356 | 0x00163 | 1 | Allowable Engine Cylinder Temperature Low Limit from Average | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 355 | 163 | 0x00163
Exhaust Temperature from Data Link | R | 357 | 0x00164 | 1 | Temperature of combustion byproducts leaving the engine, as received from another module over the CAN data link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 356 | 164 | 0x00164
Turbocharger 1 Compressor Inlet Temperature | R | 358 | 0x00165 | 1 | Temperature of the air entering the compressor side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 357 | 165 | 0x00165
Turbocharger 2 Compressor Inlet Temperature | R | 359 | 0x00166 | 1 | Temperature of the air entering the compressor side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 358 | 166 | 0x00166
Turbocharger 3 Compressor Inlet Temperature | R | 360 | 0x00167 | 1 | Temperature of the air entering the compressor side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 359 | 167 | 0x00167
Turbocharger 4 Compressor Inlet Temperature | R | 361 | 0x00168 | 1 | Temperature of the air entering the compressor side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 360 | 168 | 0x00168
Turbocharger 1 Turbine Inlet Temperature | R | 362 | 0x00169 | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 361 | 169 | 0x00169
Turbocharger 1 Turbine Outlet Temperature | R | 363 | 0x0016A | 1 | Temperature of the combustion by-products exiting the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 362 | 16A | 0x0016A
Turbocharger 2 Turbine Inlet Temperature | R | 364 | 0x0016B | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 363 | 16B | 0x0016B
Turbocharger 2 Turbine Outlet Temperature | R | 365 | 0x0016C | 1 | Temperature of the combustion by-products exiting the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 364 | 16C | 0x0016C
Turbocharger 3 Turbine Inlet Temperature | R | 366 | 0x0016D | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 365 | 16D | 0x0016D
Turbocharger 3 Turbine Outlet Temperature | R | 367 | 0x0016E | 1 | Temperature of the combustion by-products exiting the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 366 | 16E | 0x0016E
Turbocharger 4 Turbine Inlet Temperature | R | 368 | 0x0016F | 1 | Temperature of the combustion by-products entering the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 367 | 16F | 0x0016F
Turbocharger 4 Turbine Outlet Temperature | R | 369 | 0x00170 | 1 | Temperature of the combustion by-products exiting the turbine side of the turbocharger, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 368 | 170 | 0x00170
Exhaust Gas Temperature Average - Bank 2 (Right) from Data Link | R | 370 | 0x00171 | 1 | Average temperature based upon the exhaust port temperature measurements of each of the engine cylinders on the right bank before the turbocharger, as received from another module on the Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 369 | 171 | 0x00171
Exhaust Gas Temperature Average - Bank 1 (Left) from Data Link | R | 371 | 0x00172 | 1 | Average temperature based upon the exhaust port temperature measurements of each of the engine cylinders on the left bank prior to the turbocharger, as received from another module on the Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 370 | 172 | 0x00172
Engine Turbocharger 1 Compressor Outlet Temperature | R | 372 | 0x00173 | 1 | Temperature of the air or air/fuel mixture exiting the turbocharger 1 compressor outlet | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 371 | 173 | 0x00173
Cylinder #1 Ignition Transformer Secondary Output from Data Link | R | 373 | 0x00174 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #1 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 372 | 174 | 0x00174
Cylinder #2 Ignition Transformer Secondary Output from Data Link | R | 374 | 0x00175 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #2 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 373 | 175 | 0x00175
Cylinder #3 Ignition Transformer Secondary Output from Data Link | R | 375 | 0x00176 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #3 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 374 | 176 | 0x00176
Cylinder #4 Ignition Transformer Secondary Output from Data Link | R | 376 | 0x00177 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #4 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 375 | 177 | 0x00177
Cylinder #5 Ignition Transformer Secondary Output from Data Link | R | 377 | 0x00178 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #5 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 376 | 178 | 0x00178
Cylinder #6 Ignition Transformer Secondary Output from Data Link | R | 378 | 0x00179 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #6 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 377 | 179 | 0x00179
Cylinder #7 Ignition Transformer Secondary Output from Data Link | R | 379 | 0x0017A | 1 | Indicates the relative intensity of the secondary output voltage of ignition #7 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 378 | 17A | 0x0017A
Cylinder #8 Ignition Transformer Secondary Output from Data Link | R | 380 | 0x0017B | 1 | Indicates the relative intensity of the secondary output voltage of ignition #8 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 379 | 17B | 0x0017B
Cylinder #9 Ignition Transformer Secondary Output from Data Link | R | 381 | 0x0017C | 1 | Indicates the relative intensity of the secondary output voltage of ignition #9 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 380 | 17C | 0x0017C
Cylinder #10 Ignition Transformer Secondary Output from Data Link | R | 382 | 0x0017D | 1 | Indicates the relative intensity of the secondary output voltage of ignition #10 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 381 | 17D | 0x0017D
Cylinder #11 Ignition Transformer Secondary Output from Data Link | R | 383 | 0x0017E | 1 | Indicates the relative intensity of the secondary output voltage of ignition #11 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 382 | 17E | 0x0017E
Cylinder #12 Ignition Transformer Secondary Output from Data Link | R | 384 | 0x0017F | 1 | Indicates the relative intensity of the secondary output voltage of ignition #12 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 383 | 17F | 0x0017F
Cylinder #13 Ignition Transformer Secondary Output from Data Link | R | 385 | 0x00180 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #13 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 384 | 180 | 0x00180
Cylinder #14 Ignition Transformer Secondary Output from Data Link | R | 386 | 0x00181 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #14 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 385 | 181 | 0x00181
Cylinder #15 Ignition Transformer Secondary Output from Data Link | R | 387 | 0x00182 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #15 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 386 | 182 | 0x00182
Cylinder #16 Ignition Transformer Secondary Output from Data Link | R | 388 | 0x00183 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #16 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 387 | 183 | 0x00183
Cylinder #17 Ignition Transformer Secondary Output from Data Link | R | 389 | 0x00184 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #17 transformer , as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 388 | 184 | 0x00184
Cylinder #18 Ignition Transformer Secondary Output from Data Link | R | 390 | 0x00185 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #18 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 389 | 185 | 0x00185
Cylinder #19 Ignition Transformer Secondary Output from Data Link | R | 391 | 0x00186 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #19 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 390 | 186 | 0x00186
Cylinder #20 Ignition Transformer Secondary Output from Data Link | R | 392 | 0x00187 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #20 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 391 | 187 | 0x00187
Engine Gaseous Fuel Correction Factor | R | 393 | 0x00188 | 1 | A correction to a predefined gaseous fuel energy content represented as a percentage, as received from another module on the Data Link. (Actual fuel energy used is the product of gasueous fuel correction factor and the energy of the gas) | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 392 | 188 | 0x00188
Cylinder # 1 Combustion (Burn) Time | R | 394 | 0x00189 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #1 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 393 | 189 | 0x00189
Cylinder # 2 Combustion (Burn) Time | R | 395 | 0x0018A | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #2 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 394 | 18A | 0x0018A
Cylinder # 3 Combustion (Burn) Time | R | 396 | 0x0018B | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #3 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 395 | 18B | 0x0018B
Cylinder # 4 Combustion (Burn) Time | R | 397 | 0x0018C | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #4 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 396 | 18C | 0x0018C
Cylinder # 5 Combustion (Burn) Time | R | 398 | 0x0018D | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #5 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 397 | 18D | 0x0018D
Cylinder # 6 Combustion (Burn) Time | R | 399 | 0x0018E | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #6 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 398 | 18E | 0x0018E
Cylinder # 7 Combustion (Burn) Time | R | 400 | 0x0018F | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #7 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 399 | 18F | 0x0018F
Cylinder # 8 Combustion (Burn) Time | R | 401 | 0x00190 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #8 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 400 | 190 | 0x00190
Cylinder # 9 Combustion (Burn) Time | R | 402 | 0x00191 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #9 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 401 | 191 | 0x00191
Cylinder # 10 Combustion (Burn) Time | R | 403 | 0x00192 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #10 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 402 | 192 | 0x00192
Cylinder # 11 Combustion (Burn) Time | R | 404 | 0x00193 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #11 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 403 | 193 | 0x00193
Cylinder # 12 Combustion (Burn) Time | R | 405 | 0x00194 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #12 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 404 | 194 | 0x00194
Cylinder # 13 Combustion (Burn) Time | R | 406 | 0x00195 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #13 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 405 | 195 | 0x00195
Cylinder # 14 Combustion (Burn) Time | R | 407 | 0x00196 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #14 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 406 | 196 | 0x00196
Cylinder # 15 Combustion (Burn) Time | R | 408 | 0x00197 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #15 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 407 | 197 | 0x00197
Cylinder # 16 Combustion (Burn) Time | R | 409 | 0x00198 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #16 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 408 | 198 | 0x00198
Cylinder # 17 Combustion (Burn) Time | R | 410 | 0x00199 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #17 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 409 | 199 | 0x00199
Cylinder # 18 Combustion (Burn) Time | R | 411 | 0x0019A | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #18 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 410 | 19A | 0x0019A
Cylinder # 19 Combustion (Burn) Time | R | 412 | 0x0019B | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #19 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 411 | 19B | 0x0019B
Cylinder # 20 Combustion (Burn) Time | R | 413 | 0x0019C | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #20 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 412 | 19C | 0x0019C
Engine Knock (Detonation) Level | R | 414 | 0x0019D | 1 | Used to read the relative level of engine detonation | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 413 | 19D | 0x0019D
Engine Peak Knock (Detonation) Level | R | 415 | 0x0019E | 1 | Used to read the peak level of knock for the overall engine (highest knock detected out of all of the cylinders monitored). The level of knock is reported where 0% is least level of knock, and increasing levels indicate more knock | 0.1 % / bit | 0 | 0 to 6550.3% | CDL Percent 1 | 414 | 19E | 0x0019E
Engine Cylinder #1 Knock Level | R | 416 | 0x0019F | 1 | Indicates the level of knock for engine cylinder #1, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 415 | 19F | 0x0019F
Engine Cylinder #2 Knock Level | R | 417 | 0x001A0 | 1 | Indicates the level of knock for engine cylinder #2, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 416 | 1A0 | 0x001A0
Engine Cylinder #3 Knock Level | R | 418 | 0x001A1 | 1 | Indicates the level of knock for engine cylinder #3, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 417 | 1A1 | 0x001A1
Engine Cylinder #4 Knock Level | R | 419 | 0x001A2 | 1 | Indicates the level of knock for engine cylinder #4, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 418 | 1A2 | 0x001A2
Engine Cylinder #5 Knock Level | R | 420 | 0x001A3 | 1 | Indicates the level of knock for engine cylinder #5, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 419 | 1A3 | 0x001A3
Engine Cylinder #6 Knock Level | R | 421 | 0x001A4 | 1 | Indicates the level of knock for engine cylinder #6, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 420 | 1A4 | 0x001A4
Engine Cylinder #7 Knock Level | R | 422 | 0x001A5 | 1 | Indicates the level of knock for engine cylinder #7, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 421 | 1A5 | 0x001A5
Engine Cylinder #8 Knock Level | R | 423 | 0x001A6 | 1 | Indicates the level of knock for engine cylinder #8, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 422 | 1A6 | 0x001A6
Engine Cylinder #9 Knock Level | R | 424 | 0x001A7 | 1 | Indicates the level of knock for engine cylinder #9, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 423 | 1A7 | 0x001A7
Engine Cylinder #10 Knock Level | R | 425 | 0x001A8 | 1 | Indicates the level of knock for engine cylinder #10, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 424 | 1A8 | 0x001A8
Engine Cylinder #11 Knock Level | R | 426 | 0x001A9 | 1 | Indicates the level of knock for engine cylinder #11, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 425 | 1A9 | 0x001A9
Engine Cylinder #12 Knock Level | R | 427 | 0x001AA | 1 | Indicates the level of knock for engine cylinder #12, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 426 | 1AA | 0x001AA
Engine Cylinder #13 Knock Level | R | 428 | 0x001AB | 1 | Indicates the level of knock for engine cylinder #13, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 427 | 1AB | 0x001AB
Engine Cylinder #14 Knock Level | R | 429 | 0x001AC | 1 | Indicates the level of knock for engine cylinder #14, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 428 | 1AC | 0x001AC
Engine Cylinder #15 Knock Level | R | 430 | 0x001AD | 1 | Indicates the level of knock for engine cylinder #15, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 429 | 1AD | 0x001AD
Engine Cylinder #16 Knock Level | R | 431 | 0x001AE | 1 | Indicates the level of knock for engine cylinder #16, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 430 | 1AE | 0x001AE
Engine Cylinder #17 Knock Level | R | 432 | 0x001AF | 1 | Indicates the level of knock for engine cylinder #17, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 431 | 1AF | 0x001AF
Engine Cylinder #18 Knock Level | R | 433 | 0x001B0 | 1 | Indicates the level of knock for engine cylinder #18, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 432 | 1B0 | 0x001B0
Engine Cylinder #19 Knock Level | R | 434 | 0x001B1 | 1 | Indicates the level of knock for engine cylinder #19, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 433 | 1B1 | 0x001B1
Engine Cylinder #20 Knock Level | R | 435 | 0x001B2 | 1 | Indicates the level of knock for engine cylinder #20, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 434 | 1B2 | 0x001B2
Cylinder # 1 Ignition Timing | R | 436 | 0x001B3 | 1 | The ignition timing or main fuel injection timing of the cylinder #1. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 435 | 1B3 | 0x001B3
Cylinder # 2 Ignition Timing | R | 437 | 0x001B4 | 1 | The ignition timing or main fuel injection timing of the cylinder #2. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 436 | 1B4 | 0x001B4
Cylinder # 3 Ignition Timing | R | 438 | 0x001B5 | 1 | The ignition timing or main fuel injection timing of the cylinder #3. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 437 | 1B5 | 0x001B5
Cylinder # 4 Ignition Timing | R | 439 | 0x001B6 | 1 | The ignition timing or main fuel injection timing of the cylinder #4. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 438 | 1B6 | 0x001B6
Cylinder # 5 Ignition Timing | R | 440 | 0x001B7 | 1 | The ignition timing or main fuel injection timing of the cylinder #5. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 439 | 1B7 | 0x001B7
Cylinder # 6 Ignition Timing | R | 441 | 0x001B8 | 1 | The ignition timing or main fuel injection timing of the cylinder #6. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 440 | 1B8 | 0x001B8
Cylinder # 7 Ignition Timing | R | 442 | 0x001B9 | 1 | The ignition timing or main fuel injection timing of the cylinder #7. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 441 | 1B9 | 0x001B9
Cylinder # 8 Ignition Timing | R | 443 | 0x001BA | 1 | The ignition timing or main fuel injection timing of the cylinder #8. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 442 | 1BA | 0x001BA
Cylinder # 9 Ignition Timing | R | 444 | 0x001BB | 1 | The ignition timing or main fuel injection timing of the cylinder #9. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 443 | 1BB | 0x001BB
Cylinder # 10 Ignition Timing | R | 445 | 0x001BC | 1 | The ignition timing or main fuel injection timing of the cylinder #10. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 444 | 1BC | 0x001BC
Cylinder # 11 Ignition Timing | R | 446 | 0x001BD | 1 | The ignition timing or main fuel injection timing of the cylinder #11. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 445 | 1BD | 0x001BD
Cylinder # 12 Ignition Timing | R | 447 | 0x001BE | 1 | The ignition timing or main fuel injection timing of the cylinder #12. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 446 | 1BE | 0x001BE
Cylinder # 13 Ignition Timing | R | 448 | 0x001BF | 1 | The ignition timing or main fuel injection timing of the cylinder #13. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 447 | 1BF | 0x001BF
Cylinder # 14 Ignition Timing | R | 449 | 0x001C0 | 1 | The ignition timing or main fuel injection timing of the cylinder #14. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 448 | 1C0 | 0x001C0
Cylinder # 15 Ignition Timing | R | 450 | 0x001C1 | 1 | The ignition timing or main fuel injection timing of the cylinder #15. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 449 | 1C1 | 0x001C1
Cylinder # 16 Ignition Timing | R | 451 | 0x001C2 | 1 | The ignition timing or main fuel injection timing of the cylinder #16. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 450 | 1C2 | 0x001C2
Cylinder # 17 Ignition Timing | R | 452 | 0x001C3 | 1 | The ignition timing or main fuel injection timing of the cylinder #17. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 451 | 1C3 | 0x001C3
Cylinder # 18 Ignition Timing | R | 453 | 0x001C4 | 1 | The ignition timing or main fuel injection timing of the cylinder #18. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 452 | 1C4 | 0x001C4
Cylinder # 19 Ignition Timing | R | 454 | 0x001C5 | 1 | The ignition timing or main fuel injection timing of the cylinder #19. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 453 | 1C5 | 0x001C5
Cylinder # 20 Ignition Timing | R | 455 | 0x001C6 | 1 | The ignition timing or main fuel injection timing of the cylinder #20. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 454 | 1C6 | 0x001C6
Cylinder #21 Exhaust Port Temperature from Data Link | R | 456 | 0x001C7 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 455 | 1C7 | 0x001C7
Cylinder #21 Combustion (Burn) Time | R | 457 | 0x001C8 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #21 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 456 | 1C8 | 0x001C8
Cylinder #21 Ignition Timing | R | 458 | 0x001C9 | 1 | The ignition timing or main fuel injection timing of the cylinder #21. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 457 | 1C9 | 0x001C9
Cylinder #21 Ignition Transformer Secondary Output from Data Link | R | 459 | 0x001CA | 1 | Indicates the relative intensity of the secondary output voltage of ignition #21 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 458 | 1CA | 0x001CA
Engine Cylinder #21 Knock Level | R | 460 | 0x001CB | 1 | Indicates the level of knock for engine cylinder #21, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 459 | 1CB | 0x001CB
Cylinder #22 Exhaust Port Temperature from Data Link | R | 461 | 0x001CC | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 460 | 1CC | 0x001CC
Cylinder #22 Combustion (Burn) Time | R | 462 | 0x001CD | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #22 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 461 | 1CD | 0x001CD
Cylinder #22 Ignition Timing | R | 463 | 0x001CE | 1 | The ignition timing or main fuel injection timing of the cylinder #22. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 462 | 1CE | 0x001CE
Cylinder #22 Ignition Transformer Secondary Output from Data Link | R | 464 | 0x001CF | 1 | Indicates the relative intensity of the secondary output voltage of ignition #22 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 463 | 1CF | 0x001CF
Engine Cylinder #22 Knock Level | R | 465 | 0x001D0 | 1 | Indicates the level of knock for engine cylinder #22, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 464 | 1D0 | 0x001D0
Cylinder #23 Exhaust Port Temperature from Data Link | R | 466 | 0x001D1 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 465 | 1D1 | 0x001D1
Cylinder #23 Combustion (Burn) Time | R | 467 | 0x001D2 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #23 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 466 | 1D2 | 0x001D2
Cylinder #23 Ignition Timing | R | 468 | 0x001D3 | 1 | The ignition timing or main fuel injection timing of the cylinder #23. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 467 | 1D3 | 0x001D3
Cylinder #23 Ignition Transformer Secondary Output from Data Link | R | 469 | 0x001D4 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #23 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 468 | 1D4 | 0x001D4
Engine Cylinder #23 Knock Level | R | 470 | 0x001D5 | 1 | Indicates the level of knock for engine cylinder #23, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 469 | 1D5 | 0x001D5
Cylinder #24 Exhaust Port Temperature from Data Link | R | 471 | 0x001D6 | 1 | Temperature at the cylinder exhaust port of the engine, as received from another module on the CAN Data Link. | 0.03125 C / bit | -273 | -273 to 1735 C | J1939 Temperature 2 | 470 | 1D6 | 0x001D6
Cylinder #24 Combustion (Burn) Time | R | 472 | 0x001D7 | 1 | The amount of time from when the ignition of the fuel is initiated to when the fuel is completely ignited for Cylinder #24 (i.e., the flame front has propagated across the cylinder). | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 471 | 1D7 | 0x001D7
Cylinder #24 Ignition Timing | R | 473 | 0x001D8 | 1 | The ignition timing or main fuel injection timing of the cylinder #24. | 1 / 128 degree / bit | -200 degrees | -200 to 301.99 degrees | J1939 Angle 1 | 472 | 1D8 | 0x001D8
Cylinder #24 Ignition Transformer Secondary Output from Data Link | R | 474 | 0x001D9 | 1 | Indicates the relative intensity of the secondary output voltage of ignition #24 transformer, as received from another module on the Data Link. | 1% / bit | -125% | -125% to 125% | J1939 Percent 3 | 473 | 1D9 | 0x001D9
Engine Cylinder #24 Knock Level | R | 475 | 0x001DA | 1 | Indicates the level of knock for engine cylinder #24, where 0% is least level of knock and 100% is most severe level of knock. | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 474 | 1DA | 0x001DA
Engine Power Derate Relative Humidity Difference | R | 476 | 0x001DB | 1 | Indicates the current relative humidity compared to available relative humidity before engine power derate occurs. | 0.125 kPa / bit | 0 kPa | -321.27% to 321.28% | J1939 Percent 9 | 475 | 1DB | 0x001DB
Operator Inducement Torque Derate Level 1 | R | 477 | 0x001DC | 1 | This is the first torque derate that will be applied to the engine operation due to operator inducement | 0.5 kPa / bit | 0 kPa | 0 to 250% | J1939 Percent 6 | 476 | 1DC | 0x001DC
Operator Inducement Time to Torque Derate Level 1 | R | 478 | 0x001DD | 1 | This parameter provides the time until Operator Inducement Torque Derate Level 1 is activated. | 1 minute / bit | 0 | 0 to 64255 mins | SCR Operator Inducement Override Time Remaining | 477 | 1DD | 0x001DD
Operator Inducement Torque Derate Level 2 | R | 479 | 0x001DE | 1 | This is the second torque derate that will be applied to the engine operation due to operator inducement. | 0.5 kPa / bit | 0 kPa | 0 to 250% | J1939 Percent 6 | 478 | 1DE | 0x001DE
Operator Inducement Time to Torque Derate Level 2 | R | 480 | 0x001DF | 1 | This parameter provides the time until Operator Inducement Torque Derate Level 2 is activated. | 1 minute / bit | 0 | 0 to 64255 mins | SCR Operator Inducement Override Time Remaining | 479 | 1DF | 0x001DF
Operator Inducement Time to Final Inducement Action | R | 481 | 0x001E0 | 1 | Indicates the time until the inducement strategy enforces the final level of engine emissions operator inducement. The final level of inducement can include derating the engine, shutting down the engine, or restricting the engine to low idle. | 1 minute / bit | 0 | 0 to 64255 mins | SCR Operator Inducement Override Time Remaining | 480 | 1E0 | 0x001E0
Engine Average Combustion Time | R | 482 | 0x001E1 | 1 | The average combustion time of all cylinders of an engine. | 0.01 ms / bit | 0 seconds | 0 to 642.55 ms | J1939 Time 2 | 481 | 1E1 | 0x001E1
Primary Data Link Status | R | 700 | 0x002BB | 1 | Indicates any present faults on this datalink. | 00 = OK 01 = FAULT 11 = DISABLED OR NOT AVAILABLE |  |  | Data Link Status | 699 | 2BB | 0x002BB
Accessory Data Link Status | R | 701 | 0x002BC | 1 | Indicates any present faults on this datalink. | 00 = OK 01 = FAULT 11 = DISABLED OR NOT AVAILABLE |  |  | Data Link Status | 700 | 2BC | 0x002BC
Primary CAN Data Link % Bus Load | R | 702 | 0x002BD | 1 | Primary(CAN A) CAN Data Link Bus Load Percentage | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 701 | 2BD | 0x002BD
Primary CAN Data Link % Peak Bus Load | R | 703 | 0x002BE | 1 | Primary(CAN A) CAN Data Link Peak Bus Load Percentage | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 702 | 2BE | 0x002BE
Accessory CAN Data Link % Bus Load | R | 704 | 0x002BF | 1 | Accessory (CAN B) CAN Data Link Bus Load Percentage | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 703 | 2BF | 0x002BF
Accessory CAN Data Link % Peak Bus Load | R | 705 | 0x002C0 | 1 | Accessory (CAN B) CAN Data Link Peak Bus Load Percentage | 0.5 kPa / bit | 0 | 0 to 125 kPa | J1939 Percent 6 | 704 | 2C0 | 0x002C0
Ethernet Port Statistics: Rx Bytes | R | 706 | 0x002C1 | 28 | Number of Bytes receive on each Ethernet Port | "4 Regs for each Port in the following order /* PHY 0 -> CPU */ /* PHY 1 -> 2 Wire Port#A */ /* PHY 2 -> 2 Wire Port#B */ /* PHY 3 -> 4 Wire Port#1 */ /* PHY 4 -> 4 Wire Port#2 */ /* PHY 5 -> 4 Wire Port#3 */ /* PHY 6 -> 4 Wire Port#4 */" |  |  | Port Stats | 705 | 2C1 | 0x002C1
Ethernet Port Statistics: Tx Bytes | R | 734 | 0x002DD | 28 | Number of Bytes transmitted on each Ethernet Port | "4 Regs for each Port in the following order /* PHY 0 -> CPU */ /* PHY 1 -> 2 Wire Port#A */ /* PHY 2 -> 2 Wire Port#B */ /* PHY 3 -> 4 Wire Port#1 */ /* PHY 4 -> 4 Wire Port#2 */ /* PHY 5 -> 4 Wire Port#3 */ /* PHY 6 -> 4 Wire Port#4 */" |  |  | Port Stats | 733 | 2DD | 0x002DD
Ethernet Port Statistics: Rx Errors | R | 762 | 0x002F9 | 28 | Number of Errors receive on each Ethernet Port | "4 Regs for each Port in the following order /* PHY 0 -> CPU */ /* PHY 1 -> 2 Wire Port#A */ /* PHY 2 -> 2 Wire Port#B */ /* PHY 3 -> 4 Wire Port#1 */ /* PHY 4 -> 4 Wire Port#2 */ /* PHY 5 -> 4 Wire Port#3 */ /* PHY 6 -> 4 Wire Port#4 */" |  |  | Port Stats | 761 | 2F9 | 0x002F9
Ethernet Port Statistics: Tx Errors | R | 790 | 0x00315 | 28 | Number of Errors transmitted on each Ethernet Port | "4 Regs for each Port in the following order /* PHY 0 -> CPU */ /* PHY 1 -> 2 Wire Port#A */ /* PHY 2 -> 2 Wire Port#B */ /* PHY 3 -> 4 Wire Port#1 */ /* PHY 4 -> 4 Wire Port#2 */ /* PHY 5 -> 4 Wire Port#3 */ /* PHY 6 -> 4 Wire Port#4 */" |  |  | Port Stats | 789 | 315 | 0x00315
Ethernet Port Statistics: Rx Dropped | R | 818 | 0x00331 | 28 | Number of received dropped packages | "4 Regs for each Port in the following order /* PHY 0 -> CPU */ /* PHY 1 -> 2 Wire Port#A */ /* PHY 2 -> 2 Wire Port#B */ /* PHY 3 -> 4 Wire Port#1 */ /* PHY 4 -> 4 Wire Port#2 */ /* PHY 5 -> 4 Wire Port#3 */ /* PHY 6 -> 4 Wire Port#4 */" |  |  | Port Stats | 817 | 331 | 0x00331
Ethernet Port Statistics: Late Collision | R | 846 | 0x0034D | 28 | Number of Late Collisions Detected | "4 Regs for each Port in the following order /* PHY 0 -> CPU */ /* PHY 1 -> 2 Wire Port#A */ /* PHY 2 -> 2 Wire Port#B */ /* PHY 3 -> 4 Wire Port#1 */ /* PHY 4 -> 4 Wire Port#2 */ /* PHY 5 -> 4 Wire Port#3 */ /* PHY 6 -> 4 Wire Port#4 */" |  |  | Port Stats | 845 | 34D | 0x0034D
Ethernet Port Statistics: Excessive Collision | R | 874 | 0x00369 | 28 | Number of Excessive Collisions Detected | "4 Regs for each Port in the following order /* PHY 0 -> CPU */ /* PHY 1 -> 2 Wire Port#A */ /* PHY 2 -> 2 Wire Port#B */ /* PHY 3 -> 4 Wire Port#1 */ /* PHY 4 -> 4 Wire Port#2 */ /* PHY 5 -> 4 Wire Port#3 */ /* PHY 6 -> 4 Wire Port#4 */" |  |  | Port Stats | 873 | 369 | 0x00369
Ethernet Port Statistics: Tx Dropped | R | 902 | 0x00385 | 28 | Number of transmitted dropped packages | "4 Regs for each Port in the following order /* PHY 0 -> CPU */ /* PHY 1 -> 2 Wire Port#A */ /* PHY 2 -> 2 Wire Port#B */ /* PHY 3 -> 4 Wire Port#1 */ /* PHY 4 -> 4 Wire Port#2 */ /* PHY 5 -> 4 Wire Port#3 */ /* PHY 6 -> 4 Wire Port#4 */" |  |  | Port Stats | 901 | 385 | 0x00385
Ethernet 2-Wire Port A Status | R | 930 | 0x003A1 | 1 | Enable status of 2-wire port #1 | "0 = Disabled 1 = Enabled" |  |  | Boolean | 929 | 3A1 | 0x003A1
Ethernet 2-Wire Port B Status | R | 931 | 0x003A2 | 1 | Enable status of 2-wire port #2 | "0 = Disabled 1 = Enabled" |  |  | Boolean | 930 | 3A2 | 0x003A2
Ethernet 4-Wire Port #1 Status | R | 932 | 0x003A3 | 1 | Enable status of 4-wire port #1 | "0 = Disabled 1 = Enabled" |  |  | Boolean | 931 | 3A3 | 0x003A3
Ethernet 4-Wire Port #2 Status | R | 933 | 0x003A4 | 1 | Enable status of 4-wire port #2 | "0 = Disabled 1 = Enabled" |  |  | Boolean | 932 | 3A4 | 0x003A4
Ethernet 4-Wire Port #3 Status | R | 934 | 0x003A5 | 1 | Enable status of 4-wire port #3 | "0 = Disabled 1 = Enabled" |  |  | Boolean | 933 | 3A5 | 0x003A5
Ethernet 4-Wire Port #4 Status | R | 935 | 0x003A6 | 1 | Enable status of 4-wire port #4 | "0 = Disabled 1 = Enabled" |  |  | Boolean | 934 | 3A6 | 0x003A6
RS-485 Annunciator Data Link Status | R | 936 | 0x003A7 | 1 | RS-485 Annunciator Data Link Status | "0 = Disabled 1 = Enabled" |  |  | Data Link Status | 935 | 3A7 | 0x003A7
Fuel Unload Pump Active | R | 939 | 0x003AA | 1 | For the Fuel Transfer feature, indicates that the Transfer Fuel In command is active. | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 938 | 3AA | 0x003AA
Fuel Load Pump Active | R | 940 | 0x003AB | 1 | Power Factor Control Command Enable | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 939 | 3AB | 0x003AB
Power System Control Unit Type A6L3 Device Info | R | 950 | 0x003B5 | 1 | indicates ECS control unit type | Device ID MID: $164 - Single Genset Control $168 - Genset Control $169 - Genset Paralleling Control |  |  | COUNT 16 | 949 | 3B5 | 0x003B5
Power System Software Group Number A6L3 Device Info | R | 951 | 0x003B6 | 5 | Indicates Power System Software Group Number | 0x00 to 0x7F for each byte (char) |  |  | ASCII | 950 | 3B6 | 0x003B6
Power System Software Version A6L3 Device Info | R | 956 | 0x003BB | 13 | Indicates Power System Software Version | 0x00 to 0x7F for each byte (char) |  |  | ASCII | 955 | 3BB | 0x003BB
Power System Control Hardware Part Number A6L3 Device Info | R | 969 | 0x003C8 | 5 | Indicates Power System Control Hardware Part Number | 0x00 to 0x7F for each byte (char) |  |  | ASCII | 968 | 3C8 | 0x003C8
Power System Control Serial Number A6L3 Device Info | R | 974 | 0x003CD | 8 | Indicates Power System Control Serial Number | 0x00 to 0x7F for each byte (char) |  |  | ASCII | 973 | 3CD | 0x003CD
Power System Control Unit Number A6L3 Device Info | R | 982 | 0x003D5 | 1 | Indicates Power System Control Unit Number A6L3 Device Info | 1 / bit | 0 | 0 to 65535 | COUNT 16 | 981 | 3D5 | 0x003D5
Engine ID/Model | R | 983 | 0x003D6 | 9 | Indicates Engine Equipment ID | 0x00 to 0x7F for each byte (char) |  |  | ASCII | 982 | 3D6 | 0x003D6
Engine Serial Number | R | 992 | 0x003DF | 4 | Used to read the engine serial number | 0x00 to 0x7F for each byte (char) |  |  | ASCII | 991 | 3DF | 0x003DF
Software Group Part Number Engine Device Info | R | 996 | 0x003E3 | 25 | Engine Software Group Part Number | 0x00 to 0x7F for each byte (char) |  |  | ASCII | 995 | 3E3 | 0x003E3
Personality Module Part Number Engine Device Info | R | 1021 | 0x003FC | 5 | Engine Personality Module Part Number | 0x00 to 0x7F for each byte (char) |  |  | ASCII | 1020 | 3FC | 0x003FC
Engine Rating Map # | R | 1026 | 0x00401 | 1 | Engine Rating Map Number | 1 / bit | 0 | 0 to 65535 | Count 16 | 1025 | 401 | 0x00401
Fuel Pump Primer Status to Display | R | 1050 | 0x00419 | 1 | Fuel Pump Primer Status | 00 = Priming Inactive 01 = Priming Active 10 = Priming Inappropriate 11 = Data Unavailable |  |  | Fuel Priming Status | 1049 | 419 | 0x00419
Manual Fuel Priming Duration Remaining | R | 1051 | 0x0041A | 1 | Time remaining in manual fuel priming, in seconds. | 0.25 seconds / bit | 0 seconds | 0 to 62.5 seconds | J1939 Time 3 | 1050 | 41A | 0x0041A
Force Idle Status (From any source) | R | 1052 | 0x0041B | 1 | Indicates if the EMCP is in idle mode regardless of source that triggers the forced idle. | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 1051 | 41B | 0x0041B
Programmable Cycle Timer 1 Output 1 Status | R | 1053 | 0x0041C | 1 | Shows status of Output 1 as driven by this timer. Output 1 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1052 | 41C | 0x0041C
Programmable Cycle Timer 2 Output 1 Status | R | 1054 | 0x0041D | 1 | Shows status of Output 1 as driven by this timer. Output 1 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1053 | 41D | 0x0041D
Programmable Cycle Timer 3 Output 1 Status | R | 1055 | 0x0041E | 1 | Shows status of Output 1 as driven by this timer. Output 1 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1054 | 41E | 0x0041E
Programmable Cycle Timer 4 Output 1 Status | R | 1056 | 0x0041F | 1 | Shows status of Output 1 as driven by this timer. Output 1 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1055 | 41F | 0x0041F
Programmable Cycle Timer 5 Output 1 Status | R | 1057 | 0x00420 | 1 | Shows status of Output 1 as driven by this timer. Output 1 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1056 | 420 | 0x00420
Programmable Cycle Timer 6 Output 1 Status | R | 1058 | 0x00421 | 1 | Shows status of Output 1 as driven by this timer. Output 1 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1057 | 421 | 0x00421
Programmable Cycle Timer 7 Output 1 Status | R | 1059 | 0x00422 | 1 | Shows status of Output 1 as driven by this timer. Output 1 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1058 | 422 | 0x00422
Programmable Cycle Timer 1 Output 2 Status | R | 1060 | 0x00423 | 1 | Shows status of Output 2 as driven by this timer. Output 2 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1059 | 423 | 0x00423
Programmable Cycle Timer 2 Output 2 Status | R | 1061 | 0x00424 | 1 | Shows status of Output 2 as driven by this timer. Output 2 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1060 | 424 | 0x00424
Programmable Cycle Timer 3 Output 2 Status | R | 1062 | 0x00425 | 1 | Shows status of Output 2 as driven by this timer. Output 2 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1061 | 425 | 0x00425
Programmable Cycle Timer 4 Output 2 Status | R | 1063 | 0x00426 | 1 | Shows status of Output 2 as driven by this timer. Output 2 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1062 | 426 | 0x00426
Programmable Cycle Timer 5 Output 2 Status | R | 1064 | 0x00427 | 1 | Shows status of Output 2 as driven by this timer. Output 2 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1063 | 427 | 0x00427
Programmable Cycle Timer 6 Output 2 Status | R | 1065 | 0x00428 | 1 | Shows status of Output 2 as driven by this timer. Output 2 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1064 | 428 | 0x00428
Programmable Cycle Timer 7 Output 2 Status | R | 1066 | 0x00429 | 1 | Shows status of Output 2 as driven by this timer. Output 2 is used to command the Generator Circuit Breaker to close. | bits 15:2 UNUSED bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1065 | 429 | 0x00429
Programmable Cycle Timer 1 Output 3 Status | R | 1067 | 0x0042A | 1 | Programmable Cycle Timer 1 Output 3 Status | bits 15:2 UNUSED .. bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1066 | 42A | 0x0042A
Programmable Cycle Timer 2 Output 3 Status | R | 1068 | 0x0042B | 1 | Programmable Cycle Timer 2 Output 3 Status | bits 15:2 UNUSED .. bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1067 | 42B | 0x0042B
Programmable Cycle Timer 3 Output 3 Status | R | 1069 | 0x0042C | 1 | Programmable Cycle Timer 3 Output 3 Status | bits 15:2 UNUSED .. bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1068 | 42C | 0x0042C
Programmable Cycle Timer 4 Output 3 Status | R | 1070 | 0x0042D | 1 | Programmable Cycle Timer 4 Output 3 Status | bits 15:2 UNUSED .. bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1069 | 42D | 0x0042D
Programmable Cycle Timer 5 Output 3 Status | R | 1071 | 0x0042E | 1 | Programmable Cycle Timer 5 Output 3 Status | bits 15:2 UNUSED .. bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1070 | 42E | 0x0042E
Programmable Cycle Timer 6 Output 3 Status | R | 1072 | 0x0042F | 1 | Programmable Cycle Timer 6 Output 3 Status | bits 15:2 UNUSED .. bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1071 | 42F | 0x0042F
Programmable Cycle Timer 7 Output 3 Status | R | 1073 | 0x00430 | 1 | Programmable Cycle Timer 7 Output 3 Status | bits 15:2 UNUSED .. bits 1:0 Timer Status |  |  | Programmable Cycle Timer Output Status | 1072 | 430 | 0x00430
DIO Status 1 | R | 1080 | 0x00437 | 1 | Status of various Digital I/O | "Bit 0: Digital Input #1 Bit 1: Digital Input #2 . . . Bit 15 : Digital Input #16" |  |  | DIO Status 1 | 1079 | 437 | 0x00437
DIO Status 2 | R | 1081 | 0x00438 | 1 | Status of various Digital I/O | "Bit 0:Digital Output #1 Bit 1: Digital Output #2 . . Bit 11 : Digital Output #12 Bit 12 : Isolated Digital Input #1" Bits 13-15: not used |  |  | DIO Status 2 | 1080 | 438 | 0x00438
Analog Input #1 Sensor Value | R | 1082 | 0x00439 | 1 | Raw sensor value read from the input (VDC, mA, ohms, or %) | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1081 | 439 | 0x00439
Analog Input #2 Sensor Value | R | 1083 | 0x0043A | 1 | Raw sensor value read from the input (VDC, mA, ohms, or %) | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1082 | 43A | 0x0043A
Analog Input #3 Sensor Value | R | 1084 | 0x0043B | 1 | Raw sensor value read from the input (VDC, mA, ohms, or %) | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1083 | 43B | 0x0043B
Analog Input #1 Data Value | R | 1085 | 0x0043C | 2 | Data value as read from the input, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1084 | 43C | 0x0043C
Analog Input #2 Data Value | R | 1087 | 0x0043E | 2 | Data value as read from the input, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1086 | 43E | 0x0043E
Analog Input #3 Data Value | R | 1089 | 0x00440 | 2 | Data value as read from the input, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1088 | 440 | 0x00440
Analog Output #1 Data Value | R | 1091 | 0x00442 | 2 | Value to be output via analog output, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1090 | 442 | 0x00442
Analog Output #2 Data Value | R | 1093 | 0x00444 | 2 | Value to be output via analog output, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1092 | 444 | 0x00444
Analog Output #1 Output Value | R | 1095 | 0x00446 | 1 | Indicates the physical value for Analog output #1 when configured for Type Current | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1094 | 446 | 0x00446
Analog Output #2 Output Value | R | 1096 | 0x00447 | 1 | Indicates the physical value for Analog output #2 when configured for Type Current | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1095 | 447 | 0x00447
PWM Output #1 Data Value | R | 1097 | 0x00448 | 2 | Value to be output via PWM output, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1096 | 448 | 0x00448
PWM Output #2 Data Value | R | 1099 | 0x0044A | 2 | Value to be output via PWM output, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1098 | 44A | 0x0044A
PWM Output #3 Data Value | R | 1101 | 0x0044C | 2 | Value to be output via PWM output, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1100 | 44C | 0x0044C
PWM Output #1 Output Percentage | R | 1103 | 0x0044E | 1 | Indicates the output percentage for PWM Output #1 | 0.0025 % / bit | 0 | 0 to 160.6375 % | J1939 Percent 1 | 1102 | 44E | 0x0044E
PWM Output #2 Output Percentage | R | 1104 | 0x0044F | 1 | Indicates the output percentage for PWM Output #2 | 0.0025 % / bit | 0 | 0 to 160.6375 % | J1939 Percent 1 | 1103 | 44F | 0x0044F
PWM Output #3 Output Percentage | R | 1105 | 0x00450 | 1 | Indicates the output percentage for PWM Output #3 | 0.0025 % / bit | 0 | 0 to 160.6375 % | J1939 Percent 1 | 1104 | 450 | 0x00450
Gas Substitution System Enable Status | R | 1216 | 0x004BF | 1 | Indicates the status of whether the gas substitution feature is active. | $000C=Enabled $000D=Disabled |  |  | Gas Substitution Status | 1215 | 4BF | 0x004BF
Telematics Cellular Packet Data Protocol (PDP) Context Activation Status | R | 1217 | 0x004C0 | 1 | Indicates the cellular packet data protocol context activation status of the cellular device data network as detected by the PLE telematics device when connected | $000E = Active $000F = Inactive $04C8 = Missing or Unknown APN |  |  | Cellular PDP Activation Status | 1216 | 4C0 | 0x004C0
Number of GPS Satellites | R | 1218 | 0x004C1 | 1 | Indicates the number of GPS Satellites as detected by the PLE telematics device | 1 / bit | 0 | 0 to 65535 | Count 16 | 1217 | 4C1 | 0x004C1
Telematics Cellular Signal Quality | R | 1219 | 0x004C2 | 1 | Indicates the strength of the signal being received by the cellular device as detected by the PLE telematics device when connected | 1% / bit | 0% | 0 to 250% | J1939 Percent 6 | 1218 | 4C2 | 0x004C2
Telematics Satellite Communication Status | R | 1220 | 0x004C3 | 1 | Indicates the status of a communications channel with the currently selected satellite as detected by the PLE telematics device when connected | $022C = Established $022D = Not Established |  |  | Communication Status | 1219 | 4C3 | 0x004C3
Telematics Communications Modem (Satellite) Signal Quality | R | 1221 | 0x004C4 | 1 | Indicates the quality of the signal being received by the communications modem as detected by the PLE telematics device when connected | 1% / bit | 0% | 0 to 250% | J1939 Percent 6 | 1220 | 4C4 | 0x004C4
Programmable Logic Function File Name | R | 1225 | 0x004C8 | 13 | Programmable Logic Function File Name | 0x00 to 0x7F for each byte (char) |  |  | ASCII | 1224 | 4C8 | 0x004C8
Programmable Logic Function File Login Username | R | 1238 | 0x004D5 | 5 | Programmable Logic Function File Login Username | 0x00 to 0x7F for each byte (char) |  |  | ASCII | 1237 | 4D5 | 0x004D5
Programmable Logic Function File Download Time/Date | R | 1243 | 0x004DA | 3 | Programmable Logic Function File Download Time/Date | Byte 5 = J1939 Time 14 (Year) Byte 4 = J1939 Time 11 (Quarter Day) Byte 3 = J1939 Time 13 (Month) Byte 2 = J1939 Time 7 (Hour) Byte 1 = J1939 Time 6 (Minute) Byte 0 = J1939 Time 3 ( Quarter Second) |  |  | Time/Date | 1242 | 4DA | 0x004DA
Programmable Logic Function File Modified Time/Date | R | 1246 | 0x004DD | 3 | Programmable Logic Function File Modified Time/Date | Byte 5 = J1939 Time 14 (Year) Byte 4 = J1939 Time 11 (Quarter Day) Byte 3 = J1939 Time 13 (Month) Byte 2 = J1939 Time 7 (Hour) Byte 1 = J1939 Time 6 (Minute) Byte 0 = J1939 Time 3 ( Quarter Second) |  |  | Time/Date | 1245 | 4DD | 0x004DD
Emergency Inducement Override Screen Enable | R | 1249 | 0x004E0 | 1 | Indicates if an operator inducement derate is allowed to be overridden. | 00 = FALSE 01 = TRUE 10 = ERROR 11 = DISABLED OR NOT AVAILABLE |  |  | Boolean | 1248 | 4E0 | 0x004E0
Engine Emissions Operator Inducement Emergency Override Active Status | R | 1250 | 0x004E1 | 1 | Used to read the whether the feature that allows the operator to override the inducement strategies during emergencies | "0=inactive 1=active" |  |  | Emergency Override Active Status | 1249 | 4E1 | 0x004E1
Genset Control SCADA IP Address Read Octet 1 (Most Significant) | R | 1251 | 0x004E2 | 1 | Genset Control SCADA IP Address Read Octet 1 (Most Significant) |  |  |  | Horn Status by Alarms | 1250 | 4E2 | 0x004E2
Genset Control SCADA IP Address Read Octet 2 | R | 1252 | 0x004E3 | 1 | Genset Control SCADA IP Address Read Octet 2 |  |  |  | Horn Status by Alarms | 1251 | 4E3 | 0x004E3
Genset Control SCADA IP Address Read Octet 3 | R | 1253 | 0x004E4 | 1 | Genset Control SCADA IP Address Read Octet 3 |  |  |  | Horn Status by Alarms | 1252 | 4E4 | 0x004E4
Genset Control SCADA IP Address Read Octet 4 (Least Significant) | R | 1254 | 0x004E5 | 1 | Genset Control SCADA IP Address Read Octet 4 (Least Significant) |  |  |  | Horn Status by Alarms | 1253 | 4E5 | 0x004E5
Genset Control SCADA IP Mask Write Octet 1 (Most Significant) | R | 1255 | 0x004E6 | 1 | Genset Control SCADA IP Mask Write Octet 1 (Most Significant) |  |  |  | Horn Status by Alarms | 1254 | 4E6 | 0x004E6
Genset Control SCADA IP Mask Write Octet 2 | R | 1256 | 0x004E7 | 1 | Genset Control SCADA IP Mask Write Octet 2 |  |  |  | Horn Status by Alarms | 1255 | 4E7 | 0x004E7
Genset Control SCADA IP Mask Write Octet 3 | R | 1257 | 0x004E8 | 1 | Genset Control SCADA IP Mask Write Octet 3 |  |  |  | Horn Status by Alarms | 1256 | 4E8 | 0x004E8
Genset Control SCADA IP Mask Write Octet 4 (Least Significant) | R | 1258 | 0x004E9 | 1 | Genset Control SCADA IP Mask Write Octet 4 (Least Significant) |  |  |  | Horn Status by Alarms | 1257 | 4E9 | 0x004E9
RDI Status 1 | R | 1259 | 0x004EA | 1 | Status of the Remote Digital Input Status 1-16 | Bit 15 = Remote Digital inpu 16 Bit 14 = Remote Digital inpu 15 Bit 13 = Remote Digital inpu 14 Bit 12 = Remote Digital inpu 13 Bit 11 = Remote Digital inpu 12 Bit 10 = Remote Digital inpu 11 Bit 9 = Remote Digital inpu 10 Bit 8 = Remote Digital inpu 9 Bit 7 = Remote Digital inpu 8 Bit 6 = Remote Digital inpu 7 Bit 5 = Remote Digital inpu 6 Bit 4 = Remote Digital input 5 Bit 3 = Remote Digital input 4 Bit 2 = Remote Digital input 3 Bit 1 = Remote Digital input 2 Bit 0 = Remote Digital input 1 |  |  | RDI Status 1 | 1258 | 4EA | 0x004EA
RDI Status 2 | R | 1260 | 0x004EB | 1 | Status of the Remote Digital Input Status 17-32 | Bit 15 = Remote Digital inpu 16 Bit 14 = Remote Digital inpu 15 Bit 13 = Remote Digital inpu 14 Bit 12 = Remote Digital inpu 13 Bit 11 = Remote Digital inpu 12 Bit 10 = Remote Digital inpu 11 Bit 9 = Remote Digital inpu 10 Bit 8 = Remote Digital inpu 9 Bit 7 = Remote Digital inpu 8 Bit 6 = Remote Digital inpu 7 Bit 5 = Remote Digital inpu 6 Bit 4 = Remote Digital input 5 Bit 3 = Remote Digital input 4 Bit 2 = Remote Digital input 3 Bit 1 = Remote Digital input 2 Bit 0 = Remote Digital input 2 |  |  | RDI Status 2 | 1259 | 4EB | 0x004EB
RDI Status 3 | R | 1261 | 0x004EC | 1 | Status of the Remote Digital Input Status 33-48 | Bit 15 = Remote Digital inpu 16 Bit 14 = Remote Digital inpu 15 Bit 13 = Remote Digital inpu 14 Bit 12 = Remote Digital inpu 13 Bit 11 = Remote Digital inpu 12 Bit 10 = Remote Digital inpu 11 Bit 9 = Remote Digital inpu 10 Bit 8 = Remote Digital inpu 9 Bit 7 = Remote Digital inpu 8 Bit 6 = Remote Digital inpu 7 Bit 5 = Remote Digital inpu 6 Bit 4 = Remote Digital input 5 Bit 3 = Remote Digital input 4 Bit 2 = Remote Digital input 3 Bit 1 = Remote Digital input 2 Bit 0 = Remote Digital input 3 |  |  | RDI Status 3 | 1260 | 4EC | 0x004EC
RDO Status 1 | R | 1262 | 0x004ED | 1 | Status of the Remote Digital Output Status 1-16 | Bit 15 = Remote Digital inpu 16 Bit 14 = Remote Digital inpu 15 Bit 13 = Remote Digital inpu 14 Bit 12 = Remote Digital inpu 13 Bit 11 = Remote Digital inpu 12 Bit 10 = Remote Digital inpu 11 Bit 9 = Remote Digital inpu 10 Bit 8 = Remote Digital inpu 9 Bit 7 = Remote Digital inpu 8 Bit 6 = Remote Digital inpu 7 Bit 5 = Remote Digital inpu 6 Bit 4 = Remote Digital input 5 Bit 3 = Remote Digital input 4 Bit 2 = Remote Digital input 3 Bit 1 = Remote Digital input 2 Bit 0 = Remote Digital input 4 |  |  | RDO Status 1 | 1261 | 4ED | 0x004ED
RDO Status 2 | R | 1263 | 0x004EE | 1 | Status of the Remote Digital Output Status 17-32 | Bit 15 = Remote Digital inpu 32 Bit 14 = Remote Digital inpu 31 Bit 13 = Remote Digital inpu 30 Bit 12 = Remote Digital inpu 29 Bit 11 = Remote Digital inpu 28 Bit 10 = Remote Digital inpu 27 Bit 9 = Remote Digital inpu 26 Bit 8 = Remote Digital inpu 25 Bit 7 = Remote Digital inpu 24 Bit 6 = Remote Digital inpu 23 Bit 5 = Remote Digital inpu 22 Bit 4 = Remote Digital input 21 Bit 3 = Remote Digital input 20 Bit 2 = Remote Digital input 19 Bit 1 = Remote Digital input 18 Bit 0 = Remote Digital input 17 |  |  | RDO Status 2 | 1262 | 4EE | 0x004EE
RDO Status 3 | R | 1264 | 0x004EF | 1 | Status of the Remote Digital Input Status 33-48 | Bit 15 = Remote Digital inpu 48 Bit 14 = Remote Digital inpu 47 Bit 13 = Remote Digital inpu 46 Bit 12 = Remote Digital inpu 45 Bit 11 = Remote Digital inpu 44 Bit 10 = Remote Digital inpu 43 Bit 9 = Remote Digital inpu 42 Bit 8 = Remote Digital inpu 41 Bit 7 = Remote Digital inpu 40 Bit 6 = Remote Digital inpu 39 Bit 5 = Remote Digital inpu 38 Bit 4 = Remote Digital input 37 Bit 3 = Remote Digital input 36 Bit 2 = Remote Digital input 35 Bit 1 = Remote Digital input 34 Bit 0 = Remote Digital input 33 |  |  | RDO Status 3 | 1263 | 4EF | 0x004EF
Remote Analog Input #1 Sensor Value | R | 1265 | 0x004F0 | 1 | Raw sensor value read from the input (VDC, mA, ohms, or %) | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1264 | 4F0 | 0x004F0
Remote Analog Input #2 Sensor Value | R | 1266 | 0x004F1 | 1 | Raw sensor value read from the input (VDC, mA, ohms, or %) | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1265 | 4F1 | 0x004F1
Remote Analog Input #3 Sensor Value | R | 1267 | 0x004F2 | 1 | Raw sensor value read from the input (VDC, mA, ohms, or %) | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1266 | 4F2 | 0x004F2
Remote Analog Input #4 Sensor Value | R | 1268 | 0x004F3 | 1 | Raw sensor value read from the input (VDC, mA, ohms, or %) | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1267 | 4F3 | 0x004F3
Remote Analog Input #5 Sensor Value | R | 1269 | 0x004F4 | 1 | Raw sensor value read from the input (VDC, mA, ohms, or %) | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1268 | 4F4 | 0x004F4
Remote Analog Input #6 Sensor Value | R | 1270 | 0x004F5 | 1 | Raw sensor value read from the input (VDC, mA, ohms, or %) | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1269 | 4F5 | 0x004F5
Remote Analog Input #7 Sensor Value | R | 1271 | 0x004F6 | 1 | Raw sensor value read from the input (VDC, mA, ohms, or %) | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1270 | 4F6 | 0x004F6
Remote Analog Input #8 Sensor Value | R | 1272 | 0x004F7 | 1 | Raw sensor value read from the input (VDC, mA, ohms, or %) | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1271 | 4F7 | 0x004F7
Remote Analog Input #1 Data Value | R | 1273 | 0x004F8 | 2 | Data value as read from the input, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1272 | 4F8 | 0x004F8
Remote Analog Input #2 Data Value | R | 1275 | 0x004FA | 2 | Data value as read from the input, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1274 | 4FA | 0x004FA
Remote Analog Input #3 Data Value | R | 1277 | 0x004FC | 2 | Data value as read from the input, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1276 | 4FC | 0x004FC
Remote Analog Input #4 Data Value | R | 1279 | 0x004FE | 2 | Data value as read from the input, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1278 | 4FE | 0x004FE
Remote Analog Input #5 Data Value | R | 1281 | 0x00500 | 2 | Data value as read from the input, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1280 | 500 | 0x00500
Remote Analog Input #6 Data Value | R | 1283 | 0x00502 | 2 | Data value as read from the input, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1282 | 502 | 0x00502
Remote Analog Input #7 Data Value | R | 1285 | 0x00504 | 2 | Data value as read from the input, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1284 | 504 | 0x00504
Remote Analog Input #8 Data Value | R | 1287 | 0x00506 | 2 | Data value as read from the input, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1286 | 506 | 0x00506
Remote Analog Output #1 Data Value | R | 1289 | 0x00508 | 2 | Value to be output via analog output, in engineering units. | 1/256 / bit | -8224768 | -8,224,768 to 8,224,767.99609375 | Analog Data | 1288 | 508 | 0x00508
Remote Analog Output #2 Data Value | R | 1291 | 0x0050A | 2 | Value to be output via analog output, in engineering units. | 1/256 / bit | -8224767 | -8,224,768 to 8,224,767.99609376 | Analog Data | 1290 | 50A | 0x0050A
Remote Analog Output #3 Data Value | R | 1293 | 0x0050C | 2 | Value to be output via analog output, in engineering units. | 1/256 / bit | -8224766 | -8,224,768 to 8,224,767.99609377 | Analog Data | 1292 | 50C | 0x0050C
Remote Analog Output #4 Data Value | R | 1295 | 0x0050E | 2 | Value to be output via analog output, in engineering units. | 1/256 / bit | -8224765 | -8,224,768 to 8,224,767.99609378 | Analog Data | 1294 | 50E | 0x0050E
Remote Analog Output #5 Data Value | R | 1297 | 0x00510 | 2 | Value to be output via analog output, in engineering units. | 1/256 / bit | -8224764 | -8,224,768 to 8,224,767.99609379 | Analog Data | 1296 | 510 | 0x00510
Remote Analog Output #6 Data Value | R | 1299 | 0x00512 | 2 | Value to be output via analog output, in engineering units. | 1/256 / bit | -8224763 | -8,224,768 to 8,224,767.99609380 | Analog Data | 1298 | 512 | 0x00512
Remote Analog Output #7 Data Value | R | 1301 | 0x00514 | 2 | Value to be output via analog output, in engineering units. | 1/256 / bit | -8224762 | -8,224,768 to 8,224,767.99609381 | Analog Data | 1300 | 514 | 0x00514
Remote Analog Output #8 Data Value | R | 1303 | 0x00516 | 2 | Value to be output via analog output, in engineering units. | 1/256 / bit | -8224761 | -8,224,768 to 8,224,767.99609382 | Analog Data | 1302 | 516 | 0x00516
Remote Analog Output #1 Output Value | R | 1305 | 0x00518 | 1 | Indicates the physical value for Analog output #1 when configured for Type Current | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1304 | 518 | 0x00518
Remote Analog Output #2 Output Value | R | 1306 | 0x00519 | 1 | Indicates the physical value for Analog output #2 when configured for Type Current | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1305 | 519 | 0x00519
Remote Analog Output #3 Output Value | R | 1307 | 0x0051A | 1 | Indicates the physical value for Analog output #3 when configured for Type Current | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1306 | 51A | 0x0051A
Remote Analog Output #4 Output Value | R | 1308 | 0x0051B | 1 | Indicates the physical value for Analog output #4 when configured for Type Current | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1307 | 51B | 0x0051B
Remote Analog Output #5 Output Value | R | 1309 | 0x0051C | 1 | Indicates the physical value for Analog output #5 when configured for Type Current | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1308 | 51C | 0x0051C
Remote Analog Output #6 Output Value | R | 1310 | 0x0051D | 1 | Indicates the physical value for Analog output #6 when configured for Type Current | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1309 | 51D | 0x0051D
Remote Analog Output #7 Output Value | R | 1311 | 0x0051E | 1 | Indicates the physical value for Analog output #7 when configured for Type Current | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1310 | 51E | 0x0051E
Remote Analog Output #8 Output Value | R | 1312 | 0x0051F | 1 | Indicates the physical value for Analog output #8 when configured for Type Current | 1/16 / bit | -16 | -16 to 3999.9375 | Analog Sensor Value | 1311 | 51F | 0x0051F
Remote RTD Temperature #1 | R | 1313 | 0x00520 | 1 | Remote RTD Temperature #1 | 0.1 C/bit | 200 | -200 to 850 C | Remote RTD Temperature | 1312 | 520 | 0x00520
Remote RTD Temperature #2 | R | 1314 | 0x00521 | 1 | Remote RTD Temperature #2 | 0.1 C/bit | 200 | -200 to 850 C | Remote RTD Temperature | 1313 | 521 | 0x00521
Remote RTD Temperature #3 | R | 1315 | 0x00522 | 1 | Remote RTD Temperature #3 | 0.1 C/bit | 200 | -200 to 850 C | Remote RTD Temperature | 1314 | 522 | 0x00522
Remote RTD Temperature #4 | R | 1316 | 0x00523 | 1 | Remote RTD Temperature #4 | 0.1 C/bit | 200 | -200 to 850 C | Remote RTD Temperature | 1315 | 523 | 0x00523
RDI Super Status 1 | R | 1321 | 0x00528 | 1 | Indicates the Validity of Each of thre Remote Digital Input 1 to 16 | Bit15 = RDI 16 valid status . . Bit 0 = RDI 1 valid status |  |  | RDI Super Status 1 | 1320 | 528 | 0x00528
RDI Super Status 2 | R | 1322 | 0x00529 | 1 | Indicates the Validity of Each of thre Remote Digital Input 17 to 32 | Bit15 = RDI 32 valid status . . Bit 0 = RDI 17 valid status |  |  | RDI Super Status 2 | 1321 | 529 | 0x00529
RDI Super Status 3 | R | 1323 | 0x0052A | 1 | Indicates the Validity of Each of thre Remote Digital Input 33 to 48 | Bit15 = RDI 48 valid status . . Bit 0 = RDI 33 valid status |  |  | RDI Super Status 3 | 1322 | 52A | 0x0052A
RDO Super Status 1 | R | 1324 | 0x0052B | 1 | Indicates the Validity of Each of thre Remote Digital Output 1 to 16 | Bit15 = RDO 16 valid status . . Bit 0 = RDO 1 valid status |  |  | RDO Super Status 1 | 1323 | 52B | 0x0052B
RDO Super Status 2 | R | 1325 | 0x0052C | 1 | Indicates the Validity of Each of thre Remote Digital Output 17 to 32 | Bit15 = RDO 32 valid status . . Bit 0 = RDO 17 valid status |  |  | RDO Super Status 2 | 1324 | 52C | 0x0052C
RDO Super Status 3 | R | 1326 | 0x0052D | 1 | Indicates the Validity of Each of thre Remote Digital Output 33 to 48 | Bit15 = RDO 48 valid status . . Bit 0 = RDO 33 valid status |  |  | RDO Super Status 3 | 1325 | 52D | 0x0052D
Analog In Supervisor Status | R | 1327 | 0x0052E | 1 | Indicates the Validity of Each of thre Remote Anaolg input 1 to 8 | Bit 7 = Analog Input 8 valid status . . Bit 0 = Analog Input 1 valid status |  |  | Analog In Supervisor Status | 1326 | 52E | 0x0052E
Analog Out Supervisor Status | R | 1328 | 0x0052F | 1 | Indicates the Validity of Each of thre Remote Anaolg input 1 to 8 | Bit 7 = Analog Output 8 valid status . . Bit 0 = Analog Output 1 valid status |  |  | Analog Out Supervisor Status | 1327 | 52F | 0x0052F
Remote RTD Supervisor Status | R | 1329 | 0x00530 | 1 | Indicates the Validity of Each of thre Remote RTD 1 to 4 | Bit 3 = Remote RTD 4 valid status . . Bit 0 = Remote RTD 1 valid status |  |  | Remote RTD Supervisor Status | 1328 | 530 | 0x00530
Utility Average Line-Line AC RMS Voltage | R | 1330 | 0x00531 | 1 | Average Line to Line RMS voltage percent measured at the utility | 0.0078125 % / bit | -251 % | -251 to 250.99 % | AC RMS Voltage | 1329 | 531 | 0x00531
Utility Average AC RMS Frequency | R | 1331 | 0x00532 | 1 | Average AC frequency measured at the Utility. | 1 V / bit | 0 V | 0 to 64255 V | AC frequency | 1330 | 532 | 0x00532
Utility Voltage Line-Line Phase A | R | 1332 | 0x00533 | 1 | Indicates Utility line to line volatge measured at Phase A | 0.0078125 % / bit | -251 % | -251 to 250.99 % | AC RMS Voltage | 1331 | 533 | 0x00533
Utility Voltage Line-Line Phase B | R | 1333 | 0x00534 | 1 | Indicates Utility line to line volatge measured at Phase B | 0.0078125 % / bit | -251 % | -251 to 250.99 % | AC RMS Voltage | 1332 | 534 | 0x00534
Utility Voltage Line-Line Phase C | R | 1334 | 0x00535 | 1 | Indicates Utility line to line volatge measured at Phase C | 0.0078125 % / bit | -251 % | -251 to 250.99 % | AC RMS Voltage | 1333 | 535 | 0x00535
Utility Voltage Line - Neutral Phase A | R | 1335 | 0x00536 | 1 | Indicates Utility line to Neutral volatge measured at Phase A | 0.0078125 % / bit | -251 % | -251 to 250.99 % | AC RMS Voltage | 1334 | 536 | 0x00536
Utility Voltage Line - Neutral Phase B | R | 1336 | 0x00537 | 1 | Indicates Utility line to Neutral volatge measured at Phase B | 0.0078125 % / bit | -251 % | -251 to 250.99 % | AC RMS Voltage | 1335 | 537 | 0x00537
Utility Voltage Line - Neutral Phase C | R | 1337 | 0x00538 | 1 | Indicates Utility line to Neutral volatge measured at Phase C | 0.0078125 % / bit | -251 % | -251 to 250.99 % | AC RMS Voltage | 1336 | 538 | 0x00538
Utility AC Frequency Phase A | R | 1338 | 0x00539 | 1 | Indicates Utility AC frequency measured at the Phase A. | 1 V / bit | 0 V | 0 to 64255 V | AC frequency | 1337 | 539 | 0x00539
Utility AC Frequency Phase B | R | 1339 | 0x0053A | 1 | Indicates Utility AC frequency measured at the Phase B | 1 V / bit | 0 V | 0 to 64255 V | AC frequency | 1338 | 53A | 0x0053A
Utility AC Frequency Phase C | R | 1340 | 0x0053B | 1 | Indicates Utility AC frequency measured at the Phase C | 1 V / bit | 0 V | 0 to 64255 V | AC frequency | 1339 | 53B | 0x0053B
Utility AC Status | R | 1341 | 0x0053C | 1 | Indicates Utility AC status | bit 0=Not Installed bit 1=Utility Live bit 2=Utility Not Live |  |  | Utility AC Status | 1340 | 53C | 0x0053C
Power System Control Unit Type (Standby) A6L3 Device Info | R | 1350 | 0x00546 | 1 | Indicates Utility AC status | bit 0=Not Installed bit 1=Utility Live bit 2=Utility Not Live |  |  | Utility AC Status | 1349 | 545 | 0x00545
R= Read Only
W= Write Only
R/W = Read and Write
Column C = Address in Decimal (1-based, may need to add 40000)
Column D = Address in Hexadecimal (0-based, as transmitted)
Number of Registers this parameter
spans (if more than 1, the lowest
register is most significant)
Value= Register Value * Scaling + Offset
Values outside of these Limits are Error

## Change History
Version | Change History | Genset Minimum Software version required
v1.0 | Initial document | ECS_Gen_Prod_v2.0, 6620337
v1.1 | Corrected DIO status2(701) Bit mapping | ECS_Gen_Prod_v3.0, 6345095