## 200P — Port 502 Fast
Cat® ECS 200 — Recommended SCADA Modbus Registers
DEVICE: ECS 200 Paralleling (200P) | [5 empty] | PORT 502 — READ Registers — 1-Second Fast Poll
Parameter Name | R/W | Holding Register | Hex Addr | Ct | Description | Scaling (Resolution) | Offset | Limits (Ranges) | Block ID | Addr-1 | Hex | 0x Addr
⚡ BLOCK P1 — Read(2, 4) — Event/Alarm Status
System Event Lamp Status | R | 2 | 0x0001 | 1 | Indicates system lamp status | Bits 15:4 Unused Bits 3:2 Amber Lamp (Boolean) Bits 1:0 Red Lamp (Boolean) |  | Bit-packed | P1
System Horn Active Status | R | 3 | 0x0002 | 1 | Indicates audible alert horn status | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  | 0–3 | P1
Hard Shutdown Status | R | 4 | 0x0003 | 1 | Indicates hard shutdown is active | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  | 0–3 | P1
Soft Shutdown Status | R | 5 | 0x0004 | 1 | Indicates soft shutdown is active | 0 = FALSE 1 = TRUE 2 = ERROR 3 = DISABLED OR NOT AVAILABLE |  | 0–3 | P1
🔋 BLOCK P2 — Read(40, 1) — Battery
Battery Voltage | R | 40 | 0x0027 | 1 | DC battery voltage at controller input | 1/20 V / bit | 0 V | 0 to 3276.75 V | P2
🚨 BLOCK P3 — Read(101, 10) — User Alarm Groups
User Alarm Group A | R | 101 | 0x0064 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 1 = Alarm ON, 0 = Alarm OFF |  | Bit-packed | P3
User Alarm Group B | R | 102 | 0x0065 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group C | R | 103 | 0x0066 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group D | R | 104 | 0x0067 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group E | R | 105 | 0x0068 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group F | R | 106 | 0x0069 | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group G | R | 107 | 0x006A | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group H | R | 108 | 0x006B | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group I | R | 109 | 0x006C | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
User Alarm Group J | R | 110 | 0x006D | 1 | Configurable alarm group — 16 user-mapped SPN-FMI events | Bit 0–15 = Events #1–#16 |  | Bit-packed | P3
⚡ BLOCK P4 — Read(150, 10) — Generator Averages & Power
Generator Average Line-Line Voltage | R | 150 | 0x0095 | 1 | Average Line to Line RMS voltage at generator output | 1 V / bit | 0 V | 0 to 64255 V | P4
Generator Average Current | R | 152 | 0x0097 | 1 | Average RMS current at generator output | 1 A / bit | 0 A | 0 to 64255 A | P4
Engine Speed | R | 154 | 0x0099 | 1 | Engine RPM (from 200G via CAN) | 0.125 rpm / bit | 0 rpm | 0 to 8031.875 rpm | P4
Generator Total Real Power | R | 155 | 0x009A | 2 | Total real power (kW) delivered by the generator | 1 W / bit | -2000000000 W | -2B to +2.21B W | P4
↳ Generator Total Real Power (LSW) |  | 156 | 0x009B |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P4
Generator Frequency | R | 157 | 0x009C | 1 | Average AC frequency at generator output | 1/128 Hz / bit | 0 Hz | 0 to 501.99 Hz | P4
Generator Average Power Factor | R | 159 | 0x009E | 1 | Average power factor at generator output | 1/16384 / bit | -2 | -2.0 to +2.0 | P4
⚡ BLOCK P5 — Read(180, 12) — Per-Phase Voltage/Current/PF
Voltage L1-L2 | R | 180 | 0x00B3 | 1 | Line to Line RMS voltage phase A-B | 1 V / bit | 0 V | 0 to 64255 V | P5
Voltage L2-L3 | R | 181 | 0x00B4 | 1 | Line to Line RMS voltage phase B-C | 1 V / bit | 0 V | 0 to 64255 V | P5
Voltage L3-L1 | R | 182 | 0x00B5 | 1 | Line to Line RMS voltage phase C-A | 1 V / bit | 0 V | 0 to 64255 V | P5
Voltage L1-N | R | 183 | 0x00B6 | 1 | Line to Neutral RMS voltage phase A | 1 V / bit | 0 V | 0 to 64255 V | P5
Voltage L2-N | R | 184 | 0x00B7 | 1 | Line to Neutral RMS voltage phase B | 1 V / bit | 0 V | 0 to 64255 V | P5
Voltage L3-N | R | 185 | 0x00B8 | 1 | Line to Neutral RMS voltage phase C | 1 V / bit | 0 V | 0 to 64255 V | P5
Current L1 | R | 186 | 0x00B9 | 1 | RMS current phase A | 1 A / bit | 0 A | 0 to 64255 A | P5
Current L2 | R | 187 | 0x00BA | 1 | RMS current phase B | 1 A / bit | 0 A | 0 to 64255 A | P5
Current L3 | R | 188 | 0x00BB | 1 | RMS current phase C | 1 A / bit | 0 A | 0 to 64255 A | P5
Power Factor L1 | R | 189 | 0x00BC | 1 | Power factor phase A | 1/16384 / bit | -2 | -2.0 to +2.0 | P5
Power Factor L2 | R | 190 | 0x00BD | 1 | Power factor phase B | 1/16384 / bit | -2 | -2.0 to +2.0 | P5
Power Factor L3 | R | 191 | 0x00BE | 1 | Power factor phase C | 1/16384 / bit | -2 | -2.0 to +2.0 | P5
🔋 BLOCK P6 — Read(202, 5) — Reactive & Apparent Power
Generator Total Apparent Power | R | 202 | 0x00C9 | 2 | Total apparent power (kVA) delivered by the generator | 1 VA / bit | 0 VA | 0 to 4,294,967,295 VA | P6
↳ Generator Total Apparent Power (LSW) |  | 203 | 0x00CA |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P6
Generator Total Reactive Power | R | 205 | 0x00CC | 2 | Total reactive power (kVAR) delivered by the generator | 1 VAr / bit | -2000000000 VAr | -2B to +2.21B VAr | P6
↳ Generator Total Reactive Power (LSW) |  | 206 | 0x00CD |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P6
🔀 BLOCK P7 — Read(228, 5) — Operating State & Breaker
Genset Available Status | R | 228 | 0x00E3 | 1 | Whether the genset is available to the paralleling system | 0 = Not Available 1 = Available 2 = Error 3 = Disabled Or Not Available |  | 0–3 | P7
Generator Circuit Breaker Status | R | 229 | 0x00E4 | 1 | Status of the generator circuit breaker | 0 = Open 1 = Closed 2 = Error 3 = Disabled Or Not Available |  | 0–3 | P7
Operating Mode | R | 230 | 0x00E5 | 1 | Current operating mode of the genset controller | 0 = Off 1 = Manual 2 = Auto 3 = Test |  | 0–3 | P7
Genset Auto Start State | R | 231 | 0x00E6 | 1 | Current state of the automatic start/stop sequence | 0 = Init 1 = Pre Crank 2 = Starting 3 = Running 4 = Pre Cooldown 5 = Cooldown 6 = Stopping 7 = Stopped 8 = Idling |  | 0–8 | P7
Engine Run Status | R | 232 | 0x00E7 | 1 | Whether the engine is currently running | 0 = Off 1 = Running 2 = Error 3 = Disabled Or Not Available |  | 0–3 | P7
🔀 BLOCK P8 — Read(730, 9) — DBA & Sync Mode
Dead Bus Arbitration (DBA) State | R | 730 | 0x02D9 | 1 | Current state of dead bus arbitration logic | Enumerated — see SCADA manual §7.0 |  | Enumerated | P8
DBA Last Fail Reason | R | 731 | 0x02DA | 1 | Reason for last DBA failure | Enumerated failure codes |  | Enumerated | P8
Synchronize Mode / State | R | 738 | 0x02E1 | 1 | Current sync mode and state for paralleling | Enumerated — see SCADA manual §7.0 |  | Enumerated | P8
🔗 BLOCK P9 — Read(750, 31+) — System Totals & Per-Unit Data
Number of Units Online | R | 750 | 0x02ED | 1 | Total number of gensets currently online | 1 / bit | 0 | 0 to 32 | P9
Number of Units Available | R | 751 | 0x02EE | 1 | Total number of gensets available | 1 / bit | 0 | 0 to 32 | P9
Number of EPS Units Online | R | 752 | 0x02EF | 1 | Emergency Power Supply units online | 1 / bit | 0 | 0 to 32 | P9
Number of EPS Units Available | R | 753 | 0x02F0 | 1 | Emergency Power Supply units available | 1 / bit | 0 | 0 to 32 | P9
System Total Real Power | R | 756 | 0x02F3 | 2 | Combined real power from all online gensets | 1 W / bit | -2000000000 W | -2B to +2.21B W | P9
↳ System Total Real Power (LSW) |  | 757 | 0x02F4 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P9
System Total Percent Load | R | 758 | 0x02F5 | 1 | System-wide percent of rated load | 0.4 % / bit | 0 % | 0 to 100 % | P9
Gen #1 — Warning Status | R | 759 | 0x02F6 | 1 | Gen #1 has active warning | 0 = False, 1 = True |  | 0–1 | P9
Gen #1 — Shutdown Status | R | 760 | 0x02F7 | 1 | Gen #1 has active shutdown | 0 = False, 1 = True |  | 0–1 | P9
Gen #1 — DBA Status | R | 761 | 0x02F8 | 1 | Gen #1 dead bus arbitration status | Enumerated DBA states |  | Enumerated | P9
Gen #1 — Load Share Status | R | 762 | 0x02F9 | 1 | Gen #1 load share state | Enumerated load share states |  | Enumerated | P9
Gen #1 — Average Voltage | R | 763 | 0x02FA | 1 | Gen #1 average line-line voltage | 1 V / bit | 0 V | 0 to 64255 V | P9
Gen #1 — Frequency | R | 764 | 0x02FB | 1 | Gen #1 AC frequency | 1/128 Hz / bit | 0 Hz | 0 to 501.99 Hz | P9
Gen #1 — Real Power | R | 765 | 0x02FC | 2 | Gen #1 real power output | 1 W / bit | -2000000000 W | -2B to +2.21B W | P9
↳ Gen #1 — Real Power (LSW) |  | 766 | 0x02FD |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P9
Gen #1 — Breaker Status | R | 767 | 0x02FE | 1 | Gen #1 circuit breaker position | 0 = Open 1 = Closed 2 = Error 3 = N/A |  | 0–3 | P9
Gen #1 — Operating Mode | R | 768 | 0x02FF | 1 | Gen #1 operating mode | 0 = Off 1 = Manual 2 = Auto 3 = Test |  | 0–3 | P9
Gen #1 — Genset Available | R | 769 | 0x0300 | 1 | Gen #1 availability | 0 = Not Available 1 = Available |  | 0–1 | P9
Gen #1 — Engine Run Status | R | 770 | 0x0301 | 1 | Gen #1 engine running | 0 = Off 1 = Running |  | 0–1 | P9
Gen #1 — % Rated kW Load | R | 780 | 0x030B | 1 | Gen #1 percent of rated kW | 0.4 % / bit | 0 % | 0 to 100 % | P9

## 200P — Port 502 Slow
Cat® ECS 200 — Recommended SCADA Modbus Registers
DEVICE: ECS 200 Paralleling (200P) | [5 empty] | PORT 502 — READ Registers — 5–30 Second Slow Poll
Parameter Name | R/W | Holding Register | Hex Addr | Ct | Description | Scaling (Resolution) | Offset | Limits (Ranges) | Block ID | Addr-1 | Hex | 0x Addr
📈 BLOCK P10 — Read(208, 13) — Energy Meters & Ratings
Positive Real Energy (kWh) | R | 208 | 0x00CF | 2 | Accumulated positive real energy | 1 Wh / bit | 0 Wh | 0 to 4.29B Wh | P10
↳ Positive Real Energy (kWh) (LSW) |  | 209 | 0x00D0 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P10
Positive Reactive Energy (kVARh) | R | 210 | 0x00D1 | 2 | Accumulated positive reactive energy | 1 VARh / bit | 0 VARh | 0 to 4.29B VARh | P10
↳ Positive Reactive Energy (kVARh) (LSW) |  | 211 | 0x00D2 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P10
Negative Real Energy (kWh) | R | 212 | 0x00D3 | 2 | Accumulated negative real energy (reverse power) | 1 Wh / bit | 0 Wh | 0 to 4.29B Wh | P10
↳ Negative Real Energy (kWh) (LSW) |  | 213 | 0x00D4 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P10
Rated Line-Line Voltage | R | 214 | 0x00D5 | 1 | Generator nameplate rated voltage | 1 V / bit | 0 V | 0 to 64255 V | P10
Rated Line-Neutral Voltage | R | 215 | 0x00D6 | 1 | Generator nameplate rated L-N voltage | 1 V / bit | 0 V | 0 to 64255 V | P10
Rated Current | R | 216 | 0x00D7 | 1 | Generator nameplate rated current | 1 A / bit | 0 A | 0 to 64255 A | P10
Rated Frequency | R | 217 | 0x00D8 | 1 | Generator nameplate rated frequency | 1/128 Hz / bit | 0 Hz | 0 to 501.99 Hz | P10
Rated Real Power | R | 218 | 0x00D9 | 2 | Generator nameplate rated power | 1 W / bit | -2000000000 W | -2B to +2.21B W | P10
↳ Rated Real Power (LSW) |  | 219 | 0x00DA |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P10
Rated Power Factor | R | 220 | 0x00DB | 1 | Generator nameplate rated power factor | 1/16384 / bit | -2 | -2.0 to +2.0 | P10
🕐 BLOCK P11 — Read(245, 3) — Real-Time Clock
Date (MM/DD packed) | R | 245 | 0x00F4 | 1 | Controller real-time clock date | See SCADA manual §7.12 for byte decode |  | Packed bytes | P11
Year | R | 246 | 0x00F5 | 1 | Controller real-time clock year | See SCADA manual §7.12 for byte decode |  | Packed bytes | P11
Time (HH:MM:SS packed) | R | 247 | 0x00F6 | 1 | Controller real-time clock time | See SCADA manual §7.12 for byte decode |  | Packed bytes | P11
🌐 BLOCK P12 — Read(350, 1) — Data Link Status
Primary Data Link Status | R | 350 | 0x015D | 1 | CAN datalink health indicator | 00 = OK 01 = Fault 11 = Disabled Or Not Available |  | 0, 1, 3 | P12
🌐 BLOCK P13 — Read(577, 6) — Ethernet Port Status
Ethernet 2-Wire Port A Status | R | 577 | 0x0240 | 1 | SPE port A enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
Ethernet 2-Wire Port B Status | R | 578 | 0x0241 | 1 | SPE port B enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
Ethernet 4-Wire Port #1 Status | R | 579 | 0x0242 | 1 | Ethernet port #1 enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
Ethernet 4-Wire Port #2 Status | R | 580 | 0x0243 | 1 | Ethernet port #2 enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
Ethernet 4-Wire Port #3 Status | R | 581 | 0x0244 | 1 | Ethernet port #3 enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
Ethernet 4-Wire Port #4 Status | R | 582 | 0x0245 | 1 | Ethernet port #4 enable status | 0 = Disabled 1 = Enabled |  | 0–1 | P13
🔌 BLOCK P14 — Read(700, 16) — Onboard I/O Status
Onboard Discrete Input Status | R | 700 | 0x02BB | 1 | DI 1–12 status bit-packed | Bit 0–11 = DI1–DI12 1 = Active, 0 = Inactive |  | Bit-packed | P14
Onboard Isolated DI Status | R | 701 | 0x02BC | 1 | Isolated digital input status | Bit 0 = Isolated DI |  | Bit-packed | P14
Onboard Discrete Output Status | R | 702 | 0x02BD | 1 | DO 1–12 status bit-packed | Bit 0–11 = DO1–DO12 1 = Active, 0 = Inactive |  | Bit-packed | P14
Onboard Analog Input #1 Value | R | 703 | 0x02BE | 1 | AI #1 sensor value — scaling depends on Cat ET configuration | Sensor-dependent | Sensor-dependent | Sensor-dependent | P14
Onboard Analog Input #2 Value | R | 704 | 0x02BF | 1 | AI #2 sensor value | Sensor-dependent | Sensor-dependent | Sensor-dependent | P14
Onboard Analog Input #3 Value | R | 705 | 0x02C0 | 1 | AI #3 sensor value | Sensor-dependent | Sensor-dependent | Sensor-dependent | P14
Onboard Analog Output #1 Value | R | 706 | 0x02C1 | 2 | AO #1 output value | Configured output | See Cat ET | Configured | P14
↳ Onboard Analog Output #1 Value (LSW) |  | 707 | 0x02C2 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P14
Onboard Analog Output #2 Value | R | 708 | 0x02C3 | 2 | AO #2 output value | Configured output | See Cat ET | Configured | P14
↳ Onboard Analog Output #2 Value (LSW) |  | 709 | 0x02C4 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P14
Onboard PWM Output #1 Value | R | 710 | 0x02C5 | 2 | PWM #1 output value | Configured output | See Cat ET | Configured | P14
↳ Onboard PWM Output #1 Value (LSW) |  | 711 | 0x02C6 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P14
Onboard PWM Output #2 Value | R | 712 | 0x02C7 | 2 | PWM #2 output value | Configured output | See Cat ET | Configured | P14
↳ Onboard PWM Output #2 Value (LSW) |  | 713 | 0x02C8 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P14
Onboard PWM Output #3 Value | R | 714 | 0x02C9 | 2 | PWM #3 output value | Configured output | See Cat ET | Configured | P14
↳ Onboard PWM Output #3 Value (LSW) |  | 715 | 0x02CA |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | P14
⚖️ BLOCK P15 — Read(1465, 5) — LSLD State & Timers
LSLD Priority Mode | R | 1465 | 0x05B8 | 1 | Load Sense Load Demand sequencing priority | First On-First Off, Hourmeter, Manual, FIFO-EPS… |  | Enumerated | P15
LSLD State | R | 1466 | 0x05B9 | 1 | Current LSLD state | Idle, Adding, Removing, Load Shed… |  | Enumerated | P15
LSLD Desired Units Online | R | 1467 | 0x05BA | 1 | Number of units LSLD wants online | 1 / bit | 0 | 0 to 32 | P15
LSLD Add Timer Remaining | R | 1468 | 0x05BB | 1 | Seconds remaining before next unit add | 1 s / bit | 0 s | 0 to 65535 s | P15
LSLD Remove Timer Remaining | R | 1469 | 0x05BC | 1 | Seconds remaining before next unit remove | 1 s / bit | 0 s | 0 to 65535 s | P15
⚖️ BLOCK P16 — Read(1737, 1) — Load Setpoint
Generator Real Load Control Base Load Setpoint | R | 1737 | 0x06C8 | 1 | Active base load setpoint as % of rated power | 0.01 % / bit | -321.27 % | -321.27 to 321.28 % | P16
⚖️ BLOCK P17 — Read(1805, 1) — Load Control State
Generator Real Load Control State | R | 1805 | 0x070C | 1 | Current load control mode | Isochronous, Base Load, Droop, Import/Export… |  | Enumerated | P17

## 200G — Port 502 Engine
Cat® ECS 200 — Recommended SCADA Modbus Registers
DEVICE: ECS 200 Genset (200G) | [5 empty] | PORT 502 — READ Registers — Engine Sensor Data
Parameter Name | R/W | Holding Register | Hex Addr | Ct | Description | Scaling (Resolution) | Offset | Limits (Ranges) | Block ID | Addr-1 | Hex | 0x Addr
🛢️ BLOCK G1 — Read(41, 9) — Oil/Coolant/Fuel/Intake/Turbo
Oil Pressure | R | 41 | 0x0028 | 1 | Engine oil pressure | 1/128 psi / bit | 0 psi | 0 to 511 psi | G1
Coolant Temperature | R | 42 | 0x0029 | 1 | Engine coolant temperature | 1/32 °F / bit | -273 °F | -273 to 1775 °F | G1
Fuel Level | R | 43 | 0x002A | 1 | Fuel tank level | 1/2.56 % / bit | 0 % | 0 to 100 % | G1
Coolant Level | R | 44 | 0x002B | 1 | Coolant level sensor (if equipped) | 0.5 % / bit | 0 % | 0 to 100 % | G1
Oil Filter Differential Pressure | R | 45 | 0x002C | 1 | Oil filter dP (if equipped) | 1/128 psi / bit | 0 psi | 0 to 511 psi | G1
Intake Manifold Air Temperature | R | 46 | 0x002D | 1 | Intake manifold air temp | 1/32 °F / bit | -273 °F | -273 to 1775 °F | G1
Turbocharger Boost Pressure | R | 49 | 0x0030 | 1 | Turbocharger boost pressure | 1/128 psi / bit | 0 psi | 0 to 511 psi | G1
🌡️ BLOCK G2 — Read(57, 10) — Exhaust/Oil Temp/Fuel Rate/Hours
Exhaust Temperature Left Bank | R | 57 | 0x0038 | 1 | Exhaust manifold temperature — left bank | 1/32 °F / bit | -273 °F | -273 to 1775 °F | G2
Exhaust Temperature Right Bank | R | 58 | 0x0039 | 1 | Exhaust manifold temperature — right bank | 1/32 °F / bit | -273 °F | -273 to 1775 °F | G2
Oil Temperature | R | 59 | 0x003A | 1 | Engine oil temperature | 1/32 °F / bit | -273 °F | -273 to 1775 °F | G2
Fuel Consumption Rate | R | 62 | 0x003D | 1 | Instantaneous fuel consumption rate | 0.05 L/hr / bit | 0 L/hr | 0 to 3212.75 L/hr | G2
Engine Hours | R | 65 | 0x0040 | 2 | Total engine operating hours | 0.05 hr / bit | 0 hr | 0 to 210,554,060.75 hr | G2
↳ Engine Hours (LSW) |  | 66 | 0x0041 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | G2
🔧 BLOCK G3 — Read(154, 1) — Engine Speed
Engine Speed (RPM) | R | 154 | 0x0099 | 1 | Engine crankshaft speed | 0.125 rpm / bit | 0 rpm | 0 to 8031.875 rpm | G3

## 200P — Port 50200 Write
Cat® ECS 200 — Recommended SCADA Modbus Registers
DEVICE: ECS 200 Paralleling (200P) | [5 empty] | PORT 50200 — WRITE Registers — Commands & Setpoints (FC16)
Parameter Name | R/W | Holding Register | Hex Addr | Ct | Description | Scaling (Resolution) | Offset | Limits (Ranges) | Block ID | Addr-1 | Hex | 0x Addr
🚦 Alarm Acknowledge & Reset
Alarm Acknowledge Command | R | 1 | 0x0000 | 1 | Acknowledge active alarms | 0 = FALSE 1 = TRUE |  | 0–1 | W-CMD
Reset All Events Command | R | 2 | 0x0001 | 1 | Reset all active events | 0 = FALSE 1 = TRUE |  | 0–1 | W-CMD
🔀 Mode & Start/Stop Commands
Auto Mode Command | R | 102 | 0x0065 | 1 | Command genset operating mode | Enumerated mode commands |  | Enumerated | W-CMD
Start Command | R | 103 | 0x0066 | 1 | Engine start command | 0 = Off 1 = Start 2 = Error 3 = N/A |  | 0–3 | W-CMD
Stop Command | R | 104 | 0x0067 | 1 | Engine stop command | 0 = Off 1 = Stop 2 = Error 3 = N/A |  | 0–3 | W-CMD
⚖️ Setpoint Commands
Base Load Setpoint (kW) | R | 6 | 0x0005 | 2 | Target base load real power setpoint | 1 W / bit | -2000000000 W | -2B to +2.21B W | W-SET
↳ Base Load Setpoint (kW) (LSW) |  | 7 | 0x0006 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | W-SET
Base PF Setpoint | R | 8 | 0x0007 | 2 | Target base power factor setpoint | 1/16384 / bit | -2 | -2.0 to +2.0 | W-SET
↳ Base PF Setpoint (LSW) |  | 9 | 0x0008 |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | W-SET
Base VAR Setpoint | R | 10 | 0x0009 | 2 | Target base reactive power setpoint | 1 VAr / bit | -2000000000 VAr | -2B to +2.21B VAr | W-SET
↳ Base VAR Setpoint (LSW) |  | 11 | 0x000A |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | W-SET
Base Frequency Setpoint | R | 12 | 0x000B | 2 | Target frequency bias setpoint | 1/128 Hz / bit | 0 Hz | 0 to 501.99 Hz | W-SET
↳ Base Frequency Setpoint (LSW) |  | 13 | 0x000C |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | W-SET
Base Voltage Setpoint | R | 14 | 0x000D | 2 | Target voltage bias setpoint | 1/128 V / bit | 0 V | 0 to 511.99 V | W-SET
↳ Base Voltage Setpoint (LSW) |  | 15 | 0x000E |  | Low word — combine: value = (MSW << 16) ¦ LSW, then apply scaling + offset |  |  |  | W-SET

## 200P — Port 50201 Status
Cat® ECS 200 — Recommended SCADA Modbus Registers
DEVICE: ECS 200 Paralleling (200P) | [5 empty] | PORT 50201 — READ Registers — Module Status & Annunciator
Parameter Name | R/W | Holding Register | Hex Addr | Ct | Description | Scaling (Resolution) | Offset | Limits (Ranges) | Block ID | Addr-1 | Hex | 0x Addr
🌐 BLOCK S1 — Read(1, 2) — Module Online Status
Paralleling Controller Online | R | 1 | 0x0000 | 1 | Whether the paralleling controller is on the network (always True for self) | 0 = Offline 1 = Online |  | 0–1 | S1
Engine ECM Online | R | 2 | 0x0001 | 1 | Whether the engine ECM is communicating via CAN | 0 = Offline 1 = Online |  | 0–1 | S1
📊 BLOCK S2 — Read(16, 1) — Active Event Counts
Number of Active Events — Genset Controller | R | 16 | 0x000F | 1 | Count of currently active events on genset controller | 1 / bit | 0 | 0 to 65535 | S2
🔔 BLOCK S3 — Read(611, 23) — Annunciator Status Points
E-Stop Active | R | 611 | 0x0262 | 1 | Engine Auxiliary Switch Status (Emergency Stop) — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Generator Not In Auto Warning | R | 612 | 0x0263 | 1 | Generator control not in automatic mode — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Overcrank (Failure to Start) | R | 613 | 0x0264 | 1 | Engine failed to start within crank time — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Overspeed | R | 614 | 0x0265 | 1 | Engine overspeed detected — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
EPS Supplying Load | R | 615 | 0x0266 | 1 | Emergency Power Supply is active — GREEN | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Overload / Load Shed Contact | R | 616 | 0x0267 | 1 | Overload alarm or load shed active — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
High Coolant Temperature (Warning) | R | 617 | 0x0268 | 1 | Coolant temp warning threshold — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
High Coolant Temperature (Shutdown) | R | 618 | 0x0269 | 1 | Coolant temp shutdown threshold — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Coolant Temperature Warning | R | 619 | 0x026A | 1 | Coolant temp low warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Cranking Voltage Warning | R | 620 | 0x026B | 1 | Battery voltage too low for cranking — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Air Damper Shutdown | R | 621 | 0x026C | 1 | Air damper failure shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
High Battery Voltage (Warning) | R | 622 | 0x026D | 1 | Battery voltage high warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
High Battery Voltage (Shutdown) | R | 623 | 0x026E | 1 | Battery voltage high shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Battery Voltage Warning | R | 624 | 0x026F | 1 | Battery voltage low warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Oil Pressure (Warning) | R | 625 | 0x0270 | 1 | Oil pressure low warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Oil Pressure (Shutdown) | R | 626 | 0x0271 | 1 | Oil pressure low shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Coolant Level (Warning) | R | 627 | 0x0272 | 1 | Coolant level low warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Coolant Level (Shutdown) | R | 628 | 0x0273 | 1 | Coolant level low shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Fuel Level (Warning) | R | 629 | 0x0274 | 1 | Fuel level low warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Low Fuel Level (Shutdown) | R | 630 | 0x0275 | 1 | Fuel level low shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
Battery Charger AC Failure | R | 631 | 0x0276 | 1 | Battery charger AC supply failure — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
SCR SPN 4792 (Warning) | R | 632 | 0x0277 | 1 | SCR aftertreatment warning — AMBER | 0 = FALSE, 1 = TRUE |  | 0–1 | S3
SCR SPN 4792 (Shutdown) | R | 633 | 0x0278 | 1 | SCR aftertreatment shutdown — RED | 0 = FALSE, 1 = TRUE |  | 0–1 | S3

## Change History
Version | Change History | Notes
v1.0 | Initial recommended register list — curated from LEBE23522-00 SCADA Manual | ECS 200 v1.1 register list